## PDC_Rev04
[5 empty] | Changed responses shown in red |  |  |  |  | 1 = No brainer, 2 = internal discussion required, 3 = NFW
Page # reference | Section | Subsection | Requirement | Scope | CDE | Status | Landlord comment | Meta Response | Paid By | Complexity | Jbrunen Response | CRitsema Responses | DLR Final Response | Responsible Party w/i DLR
5 | §1 | N/A | Intent of Document | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Closed | Landlord will Comply, Deviate, or take Exception to any and all Meta Data Center requirements as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below. |  | - | - | - | Header item only. | N/A | N/A
5 | §2 | Bullet #1 | Landlord Design Team Expectations: Landlord shall deliver mechanical, electrical, BMS/controls, plumbing, fire protection, architectural, structural, AV, and food services design and construction administration services for the fit-out of data halls, network suites, administration, and support spaces within colocation data center facilities. | Base Build (part); TFO (part) | Comply | Open | Design services and construction administration for certain aspects of mechanical, electrical, BMS/controls, plumbing, fire protection, architectural, and structural systems will be provided as part of Tenant Fit-Out (TFO) scope of work. All design services and construction administration for AV (audio visual) systems and food service will be provided as part of Tenant Fit-Out (TFO) scope of work. Food services design, build-out, and construction administration services will not be provided by Landlord. | Not accepted. We will need to have a microkitchen put in the admin space. | Meta | 2 | Digital Realty agrees to delivery of the kitchen requirement within the office premise area as part of the TFO process. | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
5 | §2 | Bullet #2 | Landlord Design Team Expectations: Landlord Design team is required to contract or coordinate with the following partners for scopes as indicated. | TFO | Comply | Open | Comply with coordinating directly with Meta for cabling; exception is taken to contracting or coordinating with RAS - Ronald Sadusky as food services design, build-out, and construction services will not be provided by Landlord; comply with contracting or coordinating with one of Meta's listed A/V consultants. | Not accepted. We will need to have a microkitchen put in the admin space. | Meta | 2 | Digital Realty agrees to delivery of the kitchen requirement within the office premise area as part of the TFO process. | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
5 | §2 | Bullet #3 | Landlord Design Team Expectations: The Landlord is required to provide documents for Meta reviews at 100%SD, 100%DD, 50%CD, and 95%CD. Review sessions shall be open for 5 business days to allow Meta team to comment. All comments shall be adjudicated by the Design Team and provided back to the Meta Team. The Deliverable Requirements Table for Meta fit-out scope is provided as a reference. | Base Build (part); TFO (part) | Comply (part); Exception (part) | Closed | Landlord will provide 95%CD or IFC (Issued for Construction) drawings for Base Build items for Tenant review. Exception is taken to providing 100%SD, 100%DD, and 50%CD drawings to Tenant as these milestones have already been completed prior to the Effective Date of the Lease. Landlord will provide 100%SD, 100%DD, 50%CD, and 95%CD drawings for Tenant Fit-Out (TFO) scope of work items as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Digital Realty | 1 | Accepted, no further comment | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Deviate: Landlord will provide 95%CD or IFC (Issued for Construction) drawings for Base Build items for Tenant review. Landlord will provide 100%SD, 100%DD, 50%CD, and 95%CD drawings for Tenant Fit-Out (TFO) scope of work items as part of Tenant Fit-Out (TFO) scope of work. | N/A
5 | §2 | Bullet #4 | Landlord Design Team Expectations: Landlord shall deliver record docs and models for future Meta reference. | Base Build (part); TFO (part) | Comply | Closed | Record documents and models shall be in electronic form (REVIT, CAD, or PDF) and shall be in file formats mutually agreed upon by Landlord and Tenant. |  | Digital Realty | 1 | Assumed to be accepted. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
5 | §2 | Bullet #5 | Landlord Design Team Expectations: The project must adhere to all required building codes to meet local agency approval. | Base Build (part); TFO (part) | Comply | Closed | No comment. |  | Digital Realty | 1 | Assumed to be accepted. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
6 | §3 | N/A | Related Documents: Owner's Project Requirements (OPR) | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) |  | Landlord will Comply, Deviate, or take Exception to any and all Owner's Project Requirements (OPR) requirements as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below. |  |  |  | - |  | Comply | Dan Kingman
6 | §3 | N/A | Related Documents: Data Center Space Standards | Base Build | Exception | Open | A general exception is take to Meta "Data Center Space Standards" requirements. Landlord is providing and Tenant is leasing data halls, office space, storage space, and ancillary space(s) based upon Landlord's building design and space planning requirements. | Not accepted. Meta has specific requirements for operating the tenant spaces, and need those to be fit-out per our standards. | Meta | 2 | Need to review DCSS document to understand requirement. |  | Comply | Dan Kingman
6 | §3 | N/A | Related Documents: Data Center Signage Guidelines | TFO | Comply | Open | Any and all signage required by Meta to conform to Meta "Data Center Signage Guidelines" requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Meta "Data Center Signage Guidelines" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Need alignment that Meta standards will be followed for Meta occupied spaces. | Meta | 1 | Need to review DCSG to understand requirement | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
6 | §3 | N/A | Related Documents: Meta PQM Performance Spec Rev 4 | TFO | Comply (part); Deviation (part); Exception (part) | Open | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. Compliance with, deviation from, or exception to "Meta PQM Performance Spec Rev 4" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | PQM coordination can be part of TFO but expectation is LL is complying with spec. | Meta | 3 | Need to review MetaPQM to understand requirement. | Need confirmation that we can fit dual CTs and PTs on equipment (one set for DLR metering, the second set for Meta metering). | Comply | Dan Kingman
6 | §4 | N/A | Design Criteria | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Closed | Landlord will Comply, Deviate, or take Exception to any and all Meta design criteria and basis of design as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below. | - | - | - | - | Header item only. | N/A | N/A
6 | Electrical | §A | Equipment metering a. Provide CT's, Branch Circuit Monitoring and Meter Enclosures as required per Meta PQM Performance Spec requirements (metering locations to be reviewed/finalized during tenant fit out design development). i. Metering locations to include: 1. Both Normal & Gen power, OR aggregate at all MSB's. 2. Metering of the common bus at all CDP/COD boards. 3. CDP/COD reserve loop feeder breaker in MSB Reserve board . 4. Row-level branch circuit monitoring. b. Provide all required interconnects between meter enclosures and LL equipment as well as Meta gateways (DCIM head end panels). Provide dual 120V UPS backed circuits to all meter enclosures. Refer to the BMS/DCIM section of this document for additional requirements. | TFO | Comply (part); Deviation (part); Exception (part) | Open | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. Compliance with, deviation from, or exception to "Meta PQM Performance Spec Rev 4" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | PQM coordination can be part of TFO but expectation is LL is complying with spec. | Meta | 2 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
6 | Electrical | §B.a.i | Data Hall Server Row Power: 480/277V busways preferred (415/240V acceptable as alternative), lengths per rack layout. | TFO | Comply | Open | 480/277V power will not be provided. All server row power will be 415/240V. Row length and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Need feedback from Meta which is preferred, current plan is 480/415. | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply: 415/240V busway | Dan Kingman
6 | Electrical | §B.a.iii | Data Hall Server Row Power: (1) Baseline Tap Box with dual L22-30R per rack position. Tap box layout to be reviewed/finalized during tenant fit out design development. | TFO | Comply | Closed | Tap-off box configuration, quantities, and locations will be determined as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Meta | 1 | Agreed, to be incorporated in to design during TFO | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.a.iii | Data Hall Server Row Power: Row busway to be rated 800A and fed from 100% rated 800A breaker (2x400A configuration acceptable as well). Busway size to be reviewed/finalized during tenant fit out design development. | Base Build | Comply | Open | Power Distribution Unit (PDU) output breakers which feed the row busways are currently 600AF/AT. All PDU output breakers will be changed to 800AF/AT, 3P, 100% rated breakers as part of Base Building scope of work. |  | Digital Realty | 1 | Are we (DLR) covering the PDU breaker swap cost? | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply: 1x800A busway to be provided | Dan Kingman
7 | Electrical | §B.a.iv | Data Hall Server Row Power: Maximum available fault current to be 25KAIC at the server PSU input. Where 25KAIC is not achievable, Current-limiting fuse tap boxes must be used. | TFO | Comply | Closed | Tap-off box configuration, quantities, and locations will be engineered, furnished, and installed (EF&I) as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Meta | 1 | Agreed, to be incorporated in to design during TFO | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.a.v | Data Hall Server Row Power: Each row to have manual transition between primary and reserve power sources | TFO | Comply | Open | Each row will have manual transition between primary and reserve power sources located in the white space. Manual transfer switches (MTS's) will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 | No feedback from Meta, no disagreement from DLR to accommodate as part of the TFO process at Meta's cost. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.a.vi | Data Hall Server Row Power: Accessibility/maintenance: Busway horizontal access requirement is <2’ from front of the rack to the busway itself (not front of tap box). | TFO | Comply | Open | Power busway locations will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Assumed agreed, busway locations to be agreed to by Meta prior to install. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.a.vii | Data Hall Server Row Power: Each electrical distribution block shall never feed more than 2 data hall suites | Base Build | Comply | Assumed Closed | No comment. |  | Digital Realty | 1 | Assumed Closed, Each Suite Has Dedicated Infrastructure | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
7 | Electrical | §B.b.i | Reserve Connections: LL to provide a Reserve/catcher system. Each row has a manual transition to reserve; these connections may be daisy-chained such that one reserve switchboard is sufficient for all rows within a data hall. For all equipment serving more than one fault domain, the transition to reserve must be automatic. Intent is to be fully concurrently-maintable for all equipment serving more than one row, and fault tolerant for all equipment serving more than one failure domain. | Base Build (part); TFO (part) | Deviation | Open | Each PDU will have a reserve catcher system with automatic transfer switches (ATS's) as part of the Base Build. PDUs are concurrently maintanable. Manual transfer switches (MTS's) for each row can be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 | Require feedback from Meta | No response received from Meta. Digital Realty confirms deviation response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.c.i | UPS-Backed Ancillary Power: Provide dual 120V, 20A/1P, UPS backed circuits from diverse panels to meter enclosures. | TFO | Comply | Open | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. |  | Meta | 1 | Assumed to be accepted as part of Meta TFO. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.c.ii | UPS-Backed Ancillary Power: Provide dual 230V, 20A/1P, UPS backed circuits from diverse panels to cold aisle goal post receptacles. | TFO | Comply |  | Dual 230V, 20A, 1P, UPS backed circuits from diverse panels will be provided to aisle goal post receptacles as part of Tenant Fit-Out (TFO) scope of work. Hot aisle containment (HAC) will be utilized in all data halls. | Why does this say DEVIATE? Should be comply. | Meta | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
7 | Electrical | §B.c.iii | UPS-Backed Ancillary Power: Provide dual UPS-backed power to all IDF racks | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
7 | Electrical | §B.d.i | Convenience Power: Cord reels (GFCI) or convenience receptacles are required to be accessible at every row. | TFO | Comply |  | Cord reels (GFCI) or convenience receptacles will be accessible at every row and will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
7 | Electrical | §B.e.i | Grounding: Provide (2) ground bars in each data hall. Refer to technology for requirements. | Base Build | Comply |  | A minimum of two (2) ground bars will be provided in each data hall. Ground bar size, configuration, and locations shall be as stated in Landlord's electrical drawings and specifications. | Will need to be coordinated with technology during TFO to ensure it meets requirements. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
7 | Electrical | §B.f.i | Transfer Inhibit: Landlord-provided transfer inhibits for each block redundant system to ensure the reserve system is not overloaded. Include capability to prevent automatic transfer in case a bypass procedure is being performed downstream. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
7 | Electrical | §B.g.i | Power System Study: For row level breakers, please ensure the minimum settings are such: 1. LTPU: Busway full load rating (example: 400A) 2. LTD: 12, I2T on (ensure within cable / busway thermal limits) 3. STPU: 2x LTPU 4. STD: 0.2, I2T off 5. Inst: 10x LTPU | TFO | Comply |  | Row level breaker settings will be programmed as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Deviate: Lanlord will endeavor to utilize Meta minimum settings as listed; final trip unit settings will be determined via SCCS | Dan Kingman
8 | Electrical | §B.g.ii | Power System Study: Ensure breakers upstream of row level coordinate with the settings above | TFO | Comply |  | Row level breakers will be fully coordinated with all upstream breakers as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Deviate: Lanlord will endeavor to utilize Meta minimum settings as listed; final trip unit settings will be determined via SCCS | N/A
8 | Electrical | §C.a.i | Network System Row Power: (2) 415/240V dual UPS-backed busways in network suite. All remaining network busways to be single-corded, non-UPS-backed, 480/277V preferred (415/240V acceptable as alternative). Quantity of UPS backed rows to be reviewed/finalized during tenant fit out design development. | TFO | Comply |  | 480/277V power will not be provided. All network row power will be 415/240V and will be UPS backed. Quantity of rows, row length, and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §C.a.ii | Network System Row Power: Lengths per rack layout. | TFO | Comply |  | Quantity of rows, row length, and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §C.a.iii | Network System Row Power: Each busway to be rated 800A and powered from 800A, 100% rated breakers (2x 400A configuration acceptable as well). Busway size to be reviewed/finalized during tenant fit out design development. | Base Build | Comply |  | Power Distribution Unit (PDU) output breakers which feed the row busways are currently 600AF/AT. All PDU output breakers will be changed to 800AF/AT, 3P, 100% rated breakers as part of Base Building scope of work. |  | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
8 | Electrical | §C.a.iv | Network System Row Power: Tapboxes with dual L22-30R per rack position. Tap box type to match server areas. Quantities and locations per rack layout. | TFO | Comply |  | Tap-off box configuration, quantities, and locations will be determined as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Meta | 1 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §C.a.v | Network System Row Power: Accessibility/maintenance: Busway horizontal access requirement is <2’ from front of the rack to the busway itself (not front of tap box). Any larger distance requires further evaluation and alignment with Meta. | TFO | Comply |  | Power busway locations will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §C.b.i | Network System Grounding: Provide (2) ground bars in each space. Refer to technology for requirements. | Base Build | Comply |  | A minimum of two (2) ground bars will be provided in each data hall. Ground bar size, configuration, and locations shall be as stated in Landlord's electrical drawings and specifications. | Will need to be coordinated with technology during TFO to ensure it meets requirements. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
8 | Electrical | §D.a | Admin and DC Support Spaces: Refer to DSS for power and grounding requirements. | TFO | Comply |  | Any and all power and grounding for admin and data center support spaces will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §E.a | §E.a | Base Build (part); TFO (part) | Comply |  | Landlord is providing a baseline lighting design for the data halls as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline lighting package will be paid for by Meta as part of TFO NRCs. | Comply | N/A
8 | Electrical | §E.b | Lighting: Light levels to meet Meta standards in accordance with the DCC. | Base Build (part); TFO (part) | Comply |  | Landlord is providing a baseline lighting design for the data halls as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline lighting package will be paid for by Meta as part of TFO NRCs. | Comply | N/A
8 | Electrical | §F.a | Nameplates: All Meta equipment to have a nameplate that is legible from ground level | TFO | Comply |  | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §F.b | Nameplates: Nameplate to include at least the following information: i. Equipment Name ii. Fed from: iii. Source 1 and source 2 information (if applicable) | TFO | Comply |  | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements. |  | Meta | 1 | Digital Realty will follow Meta labeling schema, costs to be part of the TFO scope of work. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
8 | Electrical | §F.c | Nameplates: Examples shown below: | TFO | Comply |  | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements. |  | Meta | 1 | Digital Realty will follow Meta labeling schema, costs to be part of the TFO scope of work. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
9 | Mechanical | §A.1 | Admin Offices and Support Spaces: Office/Support space cooling design to match Meta temperature and humidity standards as listed in the Data Center Space Standards (DCSS) document. | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to office space and support space cooling design requirements per Meta "Data Center Space Standards (DCSS)" document requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
9 | Mechanical | §A.2 | Admin Offices and Support Spaces: Size supplementary cooling/heating systems, if landlord’s air handler capacity is unable to meet office/support requirements, at design ambient ASHRAE conditions (0.4%cooling, 99.6% heating) | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
9 | Mechanical | §A.3 | Admin Offices and Support Spaces: Supplementary ventilation to be based on ASHRAE 62.1 | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
9 | Mechanical | §A.4 | Admin Offices and Support Spaces: Minimum admin space humidity of 30% RH | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
9 | Mechanical | §B.1 | Studies and tooling: Development of rack loading based on site electrical distribution and review of landlord CFD (computational fluid dynamic) model to support Meta rack layout and temperature/humidity SLA requirements for all critical spaces. | TFO | Comply |  | Development of rack loading, rack location determination, and review of Landlord data hall CFD model(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
9 | Mechanical | §C.1 | Data Hall (Megapod)/Network Rooms: Provide infrastructure to support up to 100 percent (by power) air-cooling and up to an average of 80 percent (by power) liquid-cooling at the data hall level. At the individual row level technical water loops shall be sized to support 100 percent (by power) of the electrical busway capacity. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Noted that this has been agreed with the leasing team. | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Deviate: infrastructure shall be 85% (by power) air-cooling and 80% (by power) liquid cooling at the data hall level. At the individual row level technical water loops shall be sized to support 100 percent (by power) of the electrical busway capacity. | Dan Kingman
10 | Mechanical | §C.2 | Data Hall (Megapod)/Network Rooms: Front end network suites to be 100 percent (by power) air cooled day 1. Liquid cooling requirements for Front end network suites can be a deferred scope including CDU’s and piping. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 100% (by power) air-cooling at the data hall level will be provided for data halls designated as "Front End Network" data halls as part of the Base Building scope of work. Liquid cooling infrastructure within the data halls, including piping, for data halls designated as "Front End Network" data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. | Not a deviation but the liquid cooling for the FE space can be deferred, is there any benefit to deferring it or is it better to install now? | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Deviate: Front end network suites to be 100 percent (by power) air cooled day 1. Liquid cooling requirements for Front end network suites shall include tehcnical water loop piping day 1; CDUs shall be a deferred scope. | Dan Kingman
10 | Mechanical | §C.3 | Data Hall (Megapod)/Network Rooms: Any space noted as back end network suites shall mirror the data hall requirements. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Same as above. | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §C.4 | Data Hall (Megapod)/Network Rooms: The 100 percent/80 percent air-cooling/liquid-cooling infrastructure refers to cooling distribution systems inside the data halls (megapods) and network suites. Note that cooling demand can vary in any combination of 0 to 100 percent air-cooling and 0 to 80 percent liquid-cooling. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Same as item 9 | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Comply: infrastructure shall be 85% (by power) air-cooling and 80% (by power) liquid cooling at the data hall level. At the individual row level technical water loops shall be sized to support 100 percent (by power) of the electrical busway capacity. | Dan Kingman
10 | Mechanical | §D.1.i | Rack-level waterside requirements: Maximum 86°F [30°C] supply water temperature. Typical operating temperatures of 80°F [27°C]. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.ii | Rack-level waterside requirements: 18°F ΔT [10°C ΔT] waterside rack ΔT. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.iii | Rack-level waterside requirements: Minimum 0.4 GPM / kW [1.5 LPM / kW] water flow rate. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.iv | Rack-level waterside requirements: 40 PSI ΔP [241-276 kPa ΔP] pressure drop across the rack. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.v | Rack-level waterside requirements: The technical water loop header needs to be sized to align with electrical distribution capacity for that row. I.e. The technical water loop needs to be sized to assume 100% of the server capacity in the row is water cooled. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.vi | Rack-level waterside requirements: 1-¼” drops at each rack position. Elevations and positions of drops to align with layouts drawings (provided as part of BoD Documents) | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.vii | Rack-level waterside requirements: Quick connects to be BSPP thread. Approved vendors: Parker, CEJN, Safeway | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.viii | Rack-level waterside requirements: Additional 3” drops at rack positions as shown in the diagram below for rows of up to 30 servers. For rows greater than 30 servers need to agree 3” drop locations with Meta on a case by case basis. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.ix | Rack-level waterside requirements: PG25 for the TW loop to be Dowfrost LC25. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.x.a | Rack-level waterside requirements, Cleanliness: Fill flush and treatment of TW loop shall meet Dow requirements for Dow LC25. Sample of water from the TW loop once construction is complete shall be sent to Dow for approval. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
10 | Mechanical | §D.1.x.b | Rack-level waterside requirements, Cleanliness: Landlord must guarantee that no solids greater than 25 micron in size shall pass through any of the liquid cooled servers. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
11 | Mechanical | §D.2.i | Rack-level airside requirements: 65°F-85°F [18.3°C-29.4°C] supply air temperature. | Base Build | Comply |  | Airside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
11 | Mechanical | §D.2.ii | Rack-level airside requirements: 20%-80% supply air relative humidity, non-condensing. | Base Build | Comply |  | Airside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
11 | Mechanical | §D.2.iii | Rack-level airside requirements: 22°F ΔT [12.2°C ΔT] airside rack ΔT. | Base Build | Deviation |  | Airside SLAs will be as stated in Exhibit H of the Lease. Base Building design is 23°F ΔT. | Confirm what the impact would be of changing this to be 22F DT. ROM cost or schedule impact. | Digital Realty | 2 |  | Clarification needed from Meta: Exhibit H SLAs state 23°F ΔT, PDC requirements state 22°F ΔT. Which is correct? | Deviate: Exhibit H SLA = 23°F ΔT | Meta
11 | Mechanical | §D.2.iv | Rack-level airside requirements: 0.158 CFM / W [0.075 CMS / W] air flow rate. | Base Build | Deviation |  | Airside SLAs will be as stated in Exhibit H of the Lease. Base Building design is 147 cfm/kW. | Related to item above. | Digital Realty | 2 |  | Clarification needed from Meta: Exhibit H SLAs state 147 CFM/kW, PDC requirements state 158 cfm/kW. Which is correct? | Deviate: Exhibit H SLA = 147 CFM/kW | Meta
11 | Mechanical | §D.2.v | Rack-level airside requirements: MERV 8 Recirculation Filters, MERV 13 OSA Filters | Base Build | Comply |  | Airside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
11 | Mechanical | §D.3.i | Cooling distribution units (CDUs): Concurrently maintainable, feeding into a looped or manifold piping arrangement (or equivalent). | Base Build | Comply |  | Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
11 | Mechanical | §D.3.ii | Cooling distribution units (CDUs): UPS support for CDU’s is required. UPS time duration to match server shutdown time. This shall be 90 seconds or as required through discussions with the Meta server hardware team. | Base Build | Deviate |  | Waterside SLAs will be as stated in Exhibit H of the Lease. Mechanical UPS sizing and ride-through time are as required for Generator restart duration. | CDU UPS must be 5 minute minimum. | Digital Realty | 2 |  | Clarification needed from Meta: Requirement states 90-second UPS ride-through time, Meta Response comment states 5-minute UPS ride-through time. Which is correct? | Comply: defined by Exhibit H SLA | Meta
11 | Mechanical | §D.4 | Liquid cooling infrastructure inside data halls and network rooms to independently support cooling failure domain, so that cooling failure does not impact more than one failure domain unless otherwise agreed with Meta. Landlords shall provide Meta alternative liquid cooling fault domain schemes with cost and schedule impacts for review. | Base Build | Comply |  | Each data hall has a dedicated cooling infrastructure such that any data hall level cooling failure does not affect any other data hall. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
11 | Architectural | §A.1.i.a | Programming & Circulation, Admin Office space: The first building on the campus will be the main building and need desk space for 35 employees. | TFO | Comply |  | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
11 | Architectural | §A.1.i.b | Programming & Circulation, Admin Office space: All subsequent buildings on the campus will require desk space for 20 employees. | TFO | Comply |  | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
11 | Architectural | §A.1.i.c | Programming & Circulation, Admin Office space: See “Open Office” in Meta Data Center Space Standards for configuration requirements. | TFO | Comply |  | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Office/Storage Space configurations requirements per the "Open Office" section(s) of the Meta "Data Center Space Standards (DCSS)" document requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
11 | Architectural | §A.2.i | Programming & Circulation, Corridors and Pathway: Network Suites and Data Halls shall have an identified path of travel from the loading dock in which all building elements along the path can support the movement of Meta specified server racks and robotic tugs (Autonomour Guided Vehicles, or “AGV”) . Wall mounted objects (fire extinguishers, AEDs, etc) must be clear of the AGV path. | Base Build | Exception |  | A designated path-of-travel from the loading dock to the network suites and data halls will be established. Corridor width along the path-of-travel will be 8'-0" or greater. Doorway openings along the path-of-travel will be 6'-0" or greater. Certain wall mounted objects (fire extinguishers, AEDs, etc.) may protrude into the corridor and doors may swing out into the corridor. | Not accepted. Doorways along path of rack moves must be 8' wide by 9' high min. | Meta | 3 |  | Digital Realty will need to evaluate if it is possible to incease doorways along the path-of-travel to 8'-0" wide. | Comply | Dan Kingman
11 | Architectural | §A.2.ii.a | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Wall mounted objects (fire extinguishers, AEDs, etc) must be clear of the AGV path. | Base Build | Comply |  | Wall mounted objects (fire extinguishers, AEDs, etc.) will be installed in flush-mounted enclosures may protrude into the corridor. | Will these objected be outside of the 8' clear zone? If so, ok. If they protrude into the 8' zone then not accepted. | Digital Realty | 2 |  | Digital Realty response changed to "Comply". Corridor and pathway wall mounted objects shall be installed in flush mounted enclosures. Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
11 | Architectural | §A.2.ii.b | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Where possible, wall mounted objects should be consolidated on one side of the hallway. | Base Build | Comply |  | Wall mounted objects will be present on both sides of the corridor and will be installed in flush-mounted enclosures. | Will these objected be outside of the 8' clear zone? If so, ok. If they protrude into the 8' zone then not accepted. | Digital Realty | 2 |  | Digital Realty response changed to "Comply". Corridor and pathway wall mounted objects shall be installed in flush mounted enclosures. Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
11 | Architectural | §A.2.ii.c | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Should be clear of temporary obstructions (door swings into corridors, temporary laydown storage, etc.). | Base Build | Exception |  | Doors will swing out into the corridors. | Ok. Safety signage will need to added in the area of door swing zone. | Digital Realty | 2 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Exception: safety signage will be added to doors swinging into corridors | Dan Kingman
12 | Architectural | §A.2.ii.d | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: If the corridor clear width is temporarily obstructed, operations must ensure an 8’-0” clear corridor during rack movements. | Base Build | Exception |  | It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors and adequate clearances prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Agree | Meta | 1 |  | Digital Realty confirms its exception and that no changes are required. | Exception: temporary obstructions are the Tenant's responsibility | N/A
12 | Architectural | §A.2.ii.e | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: If doors swing into the corridor, the corridor should be widened to allow for 8’-0” clear with the door open. | Base Build | Exception |  | Corridor widths are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Corridor widths are fixed and cannot be widened. | Ok. Safety signage will need to added in the area of door swing zone. | Digital Realty | 2 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Exception: safety signage will be added to doors swinging into corridors | Dan Kingman
12 | Architectural | §A.2.iii | Programming & Circulation, Corridors and Pathway, AGV Types | Base Build | Exception |  | It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors and adequate clearances prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Agree | Meta | 1 |  | Digital Realty confirms its exception and that no changes are required. | Exception: AGV operations are the Tenant's responsibility | N/A
12 | Architectural | §A.2.iv.a | Freight Elevators: Located Centrally to IT Equipment Rooms and Loading Dock as possible. | Base Build | Deviation |  | Freight elevator locations are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Freight elevator locations are fixed and cannot be moved. | Accepted | Digital Realty | 1 |  | Digital Realty confirms its deviation and that no changes are required. | Deviate: Freight elevator locations are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. | N/A
12 | Architectural | §A.2.iv.b | Freight Elevators: Minimum of two per building; three is preferred | Base Build | Comply |  | The building has two (2) freight elevators. |  | Digital Realty | 1 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Comply | N/A
12 | Architectural | §A.2.iv.c | Freight Elevators: 15,000lbs. Weight capacity | Base Build | Deviation |  | Freight elevator weight capacity is 12,000 lbs. | Accepted. Confirm elevator is C rated. | Digital Realty | 2 |  | Digital Realty to confirm | Deviate: Freight elevator weight capacity is 12,000 lbs and C-rated | Dan Kingman
12 | Architectural | §A.2.iv.d | Freight Elevators: 9’ Minimum door height and 7’-3” opening width | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Comply | N/A
12 | Architectural | §A.2.iv.e | Freight Elevators: Interior cab dimensions min: 8’-4” width x 20-’10” depth and 9’-6” height. | Base Build | Deviation |  | Freight elevator cab depth is 9'-6" width x 10'-6" depth x 10'-0" height | Accepted | Digital Realty | 1 |  | Digital Realty confirms its deviation and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Deviate: Freight elevator cab depth is 9'-6" width x 10'-6" depth x 10'-0" height | N/A
12 | Architectural | §A.2.iv.f | Freight Elevators: Provide wall-mirrors around elevators as a safety measure due to heavy PIV/pedestrian traffic and blind corners | TFO | Comply |  | Wall mirrors can be provided as part of Tenant Fit-Out (TFO) scope of work. | Why is this called out as a deviation? | Meta | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
13 | Architectural | §B.1 | Audio Visual: Office Spaces should follow Meta’s current AV Standard Designs. See Meta Data Center Space Standards. Refer to Standards Hub for information on lease programming in section 3a. | TFO | Comply |  | Audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
13 | Architectural | §B.1.i | Audio Visual: One Training room allowed per campus, no Multipurpose rooms are scoped for Meta lease campuses. | TFO | Comply |  | Training room(s), multiple purpose room(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
13 | Architectural | §B.1.ii | Audio Visual: One Meet Up space with either a single monitor @ 86” or three monitors @ 55” allowed per campus. In the event of multiple Meet up spaces within campus, The AV setup will only support procurement for one AV set up per campus. | TFO | Comply |  | Meet Up space(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
13 | Architectural | §B.1.iii.a | Audio Visual: Two wall-mounted monitors per set @ 55” in the Shipping & Receiving office (none in Loading Dock area) for AV dashboards | TFO | Comply |  | Shipping & Receiving office(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
13 | Architectural | §B.1.iii.b | Audio Visual: EE service desk/helpdesk, IT vending machine, IT smart lockers, IT storage spaces | TFO | Comply |  | EE service desk(s)/helpdesk(s), IT vending machine(s), IT smart lockers, IT storage spaces and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
13 | Architectural | §C.1 | Room Numbering: All Meta dedicated rooms shall adhere to Meta Room Naming and Numbering Standards. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.2 | Room Numbering: If the landlord room numbering follows a different convention, both room numbers shall be provided on the drawings. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.3 | Room Numbering: Room numbers shall follow the guidance in the Meta Data Center Design Room Naming Standards. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.4 | Room Numbering: Ensure all spaces, including but not limited to the landlord owned spaces, are numbered, including roof areas. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.5 | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.5.i | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Meta-Owned MMR rooms shall be named MOMMR followed by a two digit designator. The MOMMR planned to route Path A/B (post 1) shall be MOMMR01 and the MOMMR planned to route Path C/D (post 2) shall be MOMMR02 | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.5.ii | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Point of Entry rooms shall be named POE followed by a two digit designator. POEs adjacent to MOMMRs shall share the same two digit designator as the MOMMR. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.5.iii | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Riser rooms shall be named RISER followed by a two digit designator. If the riser is included in the same room as an MOMMR or IDF room than the room shall use the MOMMR or IDF naming convention. The RISER planned to route Post 1 shall be named RISER01, and the RISER planned to route Post 2 shall be named RISER02. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
13 | Architectural | §C.5.iv | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Admin IDF rooms shall be named ADMINIDF followed by a two digit designator. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
14 | Architectural | §C.5.iv | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: General Service IDF rooms shall be named GSIDF followed by a two digit designator. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
14 | Architectural | §C.6 | Room Numbering: Ensure corridors are broken up as required to give each segment or turn a unique number. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
14 | Architectural | §D.1 | Room Signage: Room signage shall comply with all code and local AHJ requirements. Room signage shall contain both landlord and Meta room numbering if different than Meta standard for all Meta leased spaces. | Base Build | Comply |  | Room signage will comply with all code and local AHJ requirements. Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work.and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
14 | Architectural | §D.2 | Room Signage: META signage (placards) will only be used on all META occupied spaces and these additional landlord spaces: i. Electrical Rooms ii. UPS Rooms iii. Mechanical Galleries iv. House UPS Rooms | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
14 | Architectural | §E.1.i | Building Opening & Hardware, Door Hardware: Refer to Meta Data Center Requirements (2.1.3 Building Opening Planning & Guidelines) | TFO | Comply |  | Door hardware will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
14 | Architectural | §E.1.ii | Building Opening & Hardware, Door Hardware: Refer to the GDSS document for access control requirements. Meta security team to review for compliance with GDSS | TFO | Comply |  | Access control will be as detailed and shown in the Landlord's security drawings, plans, and specifications and will follow the Landlord's standards. Modifications to access control can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Security design must adhere to Meta requirements as outlined in the PDC. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
14 | Architectural | §E.2 | Building Opening & Hardware: Where vision panels are called out in design standards for doors, vision panels shall only be provided in interior Meta spaces, no vision panels in shared spaces. | Base Build | Comply |  | Certain common area spaces, such as conference rooms, breakout rooms, and break rooms, have doors with vision panels or glass doors and walls. | Please further clarify deviation. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
14 | Architectural | §E.3.i | Building Opening & Hardware, Doors: All doors along the rack path shall receive automatic operator and security hardware. | TFO | Comply |  | Doors along the rack path are manually operated and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door operation and hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
14 | Architectural | §E.3.ii | Building Opening & Hardware, Doors: Doors shall open the maximum extent possible and shall be double doors 8’-0” x 9'-0”. | Base Build | Deviation |  | Double doors along the rack path are 6'-0" wide x 9'-0" high and will open to the maximum extent possible. | Not accepted. Doorways along path of rack moves must be 8' wide by 9' high min. |  | 3 |  | Digital Realty to investigate. | Comply | Dan Kingman
14 | Architectural | §E.3.ii.a | Building Opening & Hardware, Doors: Controlled double doors into equipment rooms required for movement of loaded racks from docks for installation in equipment areas with adequate clearance to safely maneuver by the robotic tugs. | TFO | Comply |  | Doors along the rack path are manually operated and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door operation and hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors, adequate clearances, and proper door operation (opening) prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
14 | Architectural | §E.3.iii.a | Building Opening & Hardware, Doors, Door Hardware: Lock and latch sets, including electrified, to be heavy duty commercial mortise type | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
14 | Architectural | §E.3.iii.b | Building Opening & Hardware, Doors, Door Hardware: Use electric strikes only on aluminum/glass entrance doors as a last resort | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
14 | Architectural | §E.3.iii.c | Building Opening & Hardware, Doors, Door Hardware: Provide key override at each electric strike and electrified lock set | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
14 | Architectural | §E.3.iii.d | Building Opening & Hardware, Doors, Door Hardware: Use push pad style exit devices where required to satisfy code or local jurisdiction requirements | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
14 | Architectural | §E.3.iii.e | Building Opening & Hardware, Doors, Door Hardware: All lock cylinders shall be MEDECO High Security | TFO | Comply |  | Door hardware and lock cylinders will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware and lock cylinders can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
14 | Architectural | §E.3.iii.f | Building Opening & Hardware, Doors, Door Hardware: Lever sets: heavy-duty mortise hardware | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §E.3.iii.g | Building Opening & Hardware, Doors, Door Hardware: Hinges: stainless steel heavy duty mortised butt-hinges in accordance with manufacturer’s recommendations at swing doors | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §E.3.iii.h | Building Opening & Hardware, Doors, Door Hardware: Hinges to be tamper-resistant (NRP) throughout | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §E.3.iii.i | Building Opening & Hardware, Doors, Door Hardware: Flush bolts/coordinators on all pairs with an inactive leaf | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §E.3.iii.j | Building Opening & Hardware, Doors, Door Hardware: Closers: heavy duty hydraulic | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §E.3.iii.k | Building Opening & Hardware, Doors, Door Hardware: Provide seals for weather tightness and sound dampening | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §E.3.iii.l | Building Opening & Hardware, Doors, Door Hardware: Panic hardware: as required by code and at electrical rooms | TFO | Comply |  | Panic hardware will be provided and installed as required by code. Door hardware will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
15 | Architectural | §E.3.iii.m | Building Opening & Hardware, Doors, Door Hardware: All doors to receive REX unless otherwise indicated | TFO | Comply |  | Door functionality allows for free egress at all times. Modifications to door functionality can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
15 | Architectural | §E.3.iii.n | Building Opening & Hardware, Doors, Door Hardware: EOR responsibility to ensure all hardware is fully compatible with the door manufacturer and meets all building codes | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
15 | Architectural | §F | Meta Lighting Requirements: Includes table listing (19) space types and their associated illimination requirements. | Base Build (part), TFO (part) | Deviation |  | Landlord is providing a baseline lighting design for all spaces as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline lighting package will be paid for by Meta as part of TFO NRCs. | Comply | N/A
15 | Architectural | §G.1 | Interior Construction & Materials: Interior partitions shall receive code required fire and smoke wall ratings in addition to minimum 1-hour fire and smoke rated construction between the computer equipment rooms and office areas, between computer equipment rooms and electrical rooms, and around MPOE/BDF rooms, except where greater rating is required by code. | Base Build (part); TFO (part) | Deviation |  | Interior partitions are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Changes or reconfigurations, including changes in fire ratings, to interior partitions will be provided as part of Tenant Fit-Out (TFO) scope of work, if feasible. All partitions for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline construction package will be paid for by Meta as part of TFO NRCs. | Comply | N/A
16 | Architectural | §G.1.i | Interior Construction & Materials: See Meta Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines) | Base Build (part); TFO (part) | Deviation |  | Materials and acoustic properties are as detailed and shown in the Landlord's architectural drawings, plans, specifications, and basis of design. Changes in materials, acoustic properties, or compliance with Meta "Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines)" will be provided as part of Tenant Fit-Out (TFO) scope of work, if feasible. All materials, acoustic properties, and compliance with Meta "Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines)" for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline construction package will be paid for by Meta as part of TFO NRCs. | Comply | N/A
16 | Architectural | §G.2.i | Interior Construction & Materials, Ceiling: A structural ceiling system shall be provided in all data halls and network rooms meeting the loading requirements. The strut ceiling grid shall be braced to control sway from interior air flow and floats around the perimeter to avoid transferring forces into interior or exterior partitions. | Base Build (part), TFO (part) | Deviate |  | Base building Structural Ceiling Grid to be provided. Meta required hanging loads to be analyzed and modified as required as part of the Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline structural ceiling grid will be paid for by Meta as part of TFO NRCs. | Comply | N/A
16 | Architectural | §G.2.ii | Interior Construction & Materials, Ceiling: All areas containing food service (FS) equipment must have a finished ceiling installed overhead | TFO | Comply |  | Food services design, build-out, and construction administration services will not be provided by Landlord. | Not accepted. We will need to have a microkitchen put in the admin space. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
16 | Architectural | §G.3 | Interior Construction & Materials: Hot Aisle Containment shall allow for racks up to 8’-0” in height. Ensure airflow is blocked in the gap between racks and bottom of containment while allowing containment to move up and down slightly. Infill panels shall be provided for 10% of rack positions. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
16 | Architectural | §G.4 | Interior Construction & Materials: Review flatness & weight capacity criteria for robotics & servers with Meta | Base Build | Comply |  | Flatness and floor loading capacity will be as detailed and shown in the Landlord's structural drawings, plans, specifications, and basis of design. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Comply | N/A
16 | Architectural | §G.5 | Interior Construction & Materials: Ceilings - No Meta-specific loading criteria. Design and construct in accordance with applicable local building codes, regulations, and industry standards. | Base Build | Comply |  |  |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Comply | N/A
16 | Architectural | §H.1 | Furniture: All Furniture in Meta spaces is OFOI. AV scope must be closely coordinated with the Meta Furniture team for conference room integration. | TFO | Comply |  | All furniture and AV items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO. | Comply | Dan Kingman
16 | HAC Design | §I.1 | Rack Height Accommodation and Airflow: Hot Aisle Containment shall allow for racks up to 8'-0" in height. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
16 | HAC Design | §I.2 | Rack Height Accommodation and Airflow: Ensure airflow is blocked in the gap between racks and the bottom of containment while allowing containment to move up and down slightly. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
16 | HAC Design | §I.3 | Rack Height Accommodation and Airflow: Where IT equipment is not installed, or is not of a consistent height, an adjustable blanking panel(s) shall be provided to achieve a positive seal to mitigate air loss from the HAC. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
16 | HAC Design | §I.3.i | Rack Height Accommodation and Airflow: Sliding HAC panels shall be provided to access the cable pathways | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
16 | HAC Design | §J.1 | Aisle Layout and Clearance: Hot aisles: 6 feet with 5 feet clear | TFO | Comply |  | Hot aisle width and clearances will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
16 | HAC Design | §J.2 | Aisle Layout and Clearance: Cold aisles: 14 feet with 7 feet clear | TFO | Comply |  | Cold aisle width and clearances will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
16 | HAC Design | §J.3 | Aisle Layout and Clearance: Ensure adequate clearance between HAC columns and adjacent racks to allow for easy maintenance and access | TFO | Comply |  | Precise clearances between HAC columns and adjacent racks will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
16 | HAC Design | §K.1 | HAC System Design and Interface: Connection, panel, and construction details of the containment interface should be designed to accommodate various rack heights within a row | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
16 | HAC Design | §K.2 | HAC System Design and Interface: The TORC system should be designed to accommodate different rack heights within a row | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
17 | HAC Design | §L.1 | Safety and Code Compliance: HAC systems should be designed to meet seismic design requirements to ensure stability and integrity during earthquakes | TFO | Comply |  | Hot aisle containment (HAC) system will be designed and constructed to meet local seismic criteria and will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
17 | HAC Design | §L.2 | Safety and Code Compliance: HAC systems should be constructed using fire-resistant materials to minimize the risk of fire spread | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
17 | HAC Design | §L.3 | Safety and Code Compliance: All necessary grounding between LV racks and equipment to be provided | TFO | Comply |  | Grounding for LV racks, equipment, and hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
17 | HAC Design | §M.1 | Labeling and Identification: Installing Row Position Labels in Production Rows and Row-End Labels denoting each row per design on both ends above HAC doors | TFO | Comply |  | Row position labels, row end labels, and hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
17 | Controls & DCIM | §A.1 | System Overview: The leased facility incorporates two distinct and independently managed networks: the Landlord's operational network and Meta's dedicated Facilities Network (FacNet) | TFO | Comply |  | Installation of Meta's dedicated Facilities Network (FacNet) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
17 | Controls & DCIM | §B.1 | Landlord Owned Equipment: The control and monitoring of landlord mechanical and electrical equipment and the corresponding Building Management System (BMS) / Electrical Power Monitoring System (EPMS) shall be owned, operated and maintained by the Landlord. This should be developed in the base build scope of work. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
17 | Controls & DCIM | §B.2 | Landlord Owned Equipment: The landlord shall allow for Web access (READ – ONLY) to Meta users to access both the landlords BMS and EPMS. | Base Build | Comply |  | Access to Landlord's BMS and EPMS will be provided via web portal and via API(s). |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | Ryan Young
17 | Controls & DCIM | §C.1 | Meta FacNet and Data Center Infrastructure Management (DCIM): Integration with Meta's DCIM system will involve monitoring all specified electrical parameters to meet both Dynamo and line of demarcation requirements. Additionally, it will monitor critical environmental conditions within essential spaces to ensure compliance with Service Level Agreements (SLAs). | TFO | Comply (part); Deviation (part); Exception (part) |  | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to monitoring all specified electrical parameters to meet Dynamo and line of demarcation requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
17 | Controls & DCIM | §C.1.i | Meta FacNet and Data Center Infrastructure Management (DCIM): Note: Dynamo is a real-time power monitoring and protection reliability system that protects Meta’s power distribution network from power overages, spikes, and unplanned power surges. | TFO | Comply (part); Deviation (part); Exception (part) |  | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to monitoring all specified electrical parameters to meet Dynamo and line of demarcation requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
17 | Controls & DCIM | §C.2 | Meta FacNet and Data Center Infrastructure Management (DCIM): Each DCIM monitoring point and alert must be thoroughly tested and verified through the DCIM tooling with Ignition. | TFO | Comply (part); Deviation (part); Exception (part) |  | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Meta DCIM monitoring point and alerting testing and verification requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
17 | Controls & DCIM | §C.3 | Meta FacNet and Data Center Infrastructure Management (DCIM): DCIM integration point naming must align with DCIM naming standards (BMS-PLAN-348 – FDM Playbook Rev 1.0). | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | DCIM integration point naming will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's BMS and EPMS point naming and numbering standards. Compliance with, deviation from, or exception to dual naming, re-naming, or aligning with Meta DCIM naming standards per BMS-PLAN-348 - FDM Playbook Rev 1.0 will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
17 | Controls & DCIM | §C.3.i | Meta FacNet and Data Center Infrastructure Management (DCIM): If LL equipment naming differs from DCIM integration point naming, label containing DCIM point name is to be provided on equipment being integrated. | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | DCIM integration point naming will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's BMS and EPMS point naming and numbering standards. Compliance with, deviation from, or exception to providing equipment labeling with DCIM, BMS, or EPMS point name will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
17 | Controls & DCIM | §C.4.i | Electrical Monitoring - DCIM: Meta dedciated Power Quality Meters (PQM's) for Landlord owned MSB's. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
17 | Controls & DCIM | §C.4.i.a | Electrical Monitoring - DCIM: Separate meter enclosure shall be furnished with a monitored tamper switch. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.4.i.b | Electrical Monitoring - DCIM: PQM to be wired (Modbus RS485) to a Meta dedicated gateway panel located within Meta space. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.4.i.c | Electrical Monitoring - DCIM: Gateway panel shall connect directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.4.ii | Electrical Monitoring - DCIM: Meta dedciated PQM for Landlord PDU (Power Distribution Unit) (or equivalent line of demarcation) with branch circuit monitoring for row level metering. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.4.ii.a | Electrical Monitoring - DCIM: PDU's will follow the same physical and network security requirements as MSB PQM (e.g., separate enclosure and wired to gateway panel) unless meter brick is located within Meta secure space, in which case it can connect direct to Meta’s facility network (FacNet). | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.4.ii.b | Electrical Monitoring - DCIM: Modbus TCP/IP integration to Meta’s facility network (FacNet). | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.i | Mechanical Monitoring - DCIM: Data Hall | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.i.a | Mechanical Monitoring - DCIM: Temperature and Humidity monitoring for every cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.i.a.1 | Mechanical Monitoring - DCIM: Instruments to be provided with magnet backing and sufficient cable slack to allow placement at any rack position in the cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.i.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the data hall. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.i.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.i.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.ii | Mechanical Monitoring - DCIM: Network Core Room/s | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.ii.a | Mechanical Monitoring - DCIM: Temperature and Humidity monitoring for every cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.ii.a.1 | Mechanical Monitoring - DCIM: Instruments to be provided with magnet backing and sufficient cable slack to allow placement at any rack position in the cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.ii.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the room. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.ii.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.ii.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.iii | Mechanical Monitoring - DCIM: Technical Water | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a | Mechanical Monitoring - DCIM: The following is to be monitored: | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Supply Water Temperature | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Return Water Temperature | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Differential Pressure | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Flow Rate | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.iii.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the data hall. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
18 | Controls & DCIM | §C.5.iii.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
19 | Controls & DCIM | §C.5.iii.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
19 | Controls & DCIM | §C.5.iv | Mechanical Monitoring - DCIM: Cooling Distribution Units (where applicable) | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
19 | Controls & DCIM | §C.5.iv.a | Mechanical Monitoring - DCIM: The CDUs shall be monitored and controlled (where applicable) by the landlords BMS. | TFO | Comply (part); Deviation (part) |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. The Landlord BMS will monitor and report on CDU operation; however, CDU control will be via separate controllers and control network (top-level Landlord BMS is 'observe and report' only). | [BW] Please confirm control of CDU is done by the landlord regardless if it's a separate controller and/or network. Meta will not be controlling the CDUs. | Meta | 1 |  | Confirmed, Digital Realty will operate the CDUs. Digital Realty confirms our response and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Ryan Young
19 | Controls & DCIM | §C.6.i | Meta FacNet Security: Meta requires that all products, equipment, systems, components, and subcomponents comply with strict network compatibility and security requirements. Devices must be reviewed and approved by submitting Exhibit L, which includes detailed compliance forms such as the Product Compliance Form, Communications System Compliance Form, Component Compliance Form, and supporting documentation like communication diagrams and product data sheets. This submission ensures that devices meet Meta's network and security standards before approval for use. | TFO | Comply |  | Landlord will submit Exhibit L forms as required for Meta's review and approval. Submission of the Exhibit L forms and compliance with, deviation from, or exception to Meta's requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Comply | Dan Kingman
19 | Security | §A.a | General: Physical security, including guard force, operational policies/procedures, access controls, badging, intrusion detection and video surveillance will be the primary responsibility of the Landlord, unless otherwise noted in the lease. | Base Build | Comply |  | No comment. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that security is a Landlord responsibility and will be provided as part of the Base Build. Compliance with, deviation from, or exception to specific requirements in the "Security" will be stated for each individual requirement. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Jason Brunen
19 | Security | §A.b | General: All security requirements within this document, with the exception of those installed as part of the Meta fit out, are required at lease commencement. Any exceptions must be reviewed and approved by Meta. | Base Build | Comply |  | Compliance with, deviation from, or exception to any Meta Security requirements for each Program Design Criteria (PDC) section, subsection, or line item is as stated below. Installation of equipment to support each PDC security requirement will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty response changed to "Comply". Digital Realty confirms that it will review security requirements with Meta. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Jason Brunen
19 | Security | §A.c | General: Security requirements that are part of the Meta Fit Out are required to be active before Meta Fit out completion. | TFO | Comply |  | Compliance with, deviation from, or exception to any Meta Security requirements for each Program Design Criteria (PDC) section, subsection, or line item is as stated below. Installation of equipment to support each PDC security requirement will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty response changed to "Comply". Digital Realty confirms that it will review security requirements with Meta. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Jason Brunen
19 | Security | §B.a | Compliance: The landlord shall comply with the latest ISO/IEC 27001 Information Technology -Security Techniques - Information Security Management Systems - Requirements. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
19 | Security | §B.b | Compliance: The Landlord shall comply and provide evidence of compliance and certification on an annual basis. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
19 | Security | §B.c | Compliance: The Landlord shall comply and provide evidence of compliance with the SOC2 Standards on an annual basis. | Base Build | Comply |  | The initial evidence of compliance (SOC2 report) will be provided once the facility has been in operation for one (1) full calendar year (e.g., if the facility is completed in October 2026, the initial SOC2 report will be for 2027 and will be provided in 2028). Landlord can provide bridging letters as required by Tenant. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
19 | Security | §C.a | Submittals: The Landlord shall provide project design drawings, specifications and commissioning reports to Meta for review and comment throughout the design and construction process to ensure compliance with the security requirements included in the Lease Agreement. | Base Build (part), TFO (part) | Comply |  | Submittals for security related items for the Base Build scope-of-work will be provided by Landlord. Submittals for security related items for the Tenant Fit-Out (TFO) scope-of-work will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Landlord reserves the right to reasonably redact submittal information to the degree that it does not impact Meta's ability to evaluate for compliance to requirements. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
20 | Security | §C.a | Coordination & Inspections: Landlord shall communicate the following non-design & design related information to Meta Security prior to the design kick off date: i. Team member roles & responsibilities. ii. Paths of escalation. iii. Distribution Lists for drawing packages. iv. Security BoD (Basis of Design) or Building Security Narrative. v. List of Landlord approved security devices to be deployed (model/ part number, etc…) | Base Build (part), TFO (part) | Comply |  | Information for security related items for the Base Build scope-of-work will be provided by Landlord. Information for security related items for the Tenant Fit-Out (TFO) scope-of-work will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Landlord reserves the right to reasonably redact submittal information to the degree that it does not impact Meta's ability to evaluate for compliance to requirements. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
20 | Security | §C.b | Coordination & Inspections: During design, Landlord shall ensure that all information communicated to Meta Security for general coordination (e.g., design drawings, specifications, security device selection & installation/commissioning, construction schedules, supporting infrastructure, space hand-over dates, etc.) are based on the most recent version of the design to facilitate efficient coordination between Security, Meta’s design teams, and the landlord’s security designer. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
20 | Security | §C.c | Coordination & Inspections: If Meta fitout security designer differs from base build security designers, ensure coordination between security design occurs. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
20 | Security | §C.d | Coordination & Inspections: During construction, regular fortnightly coordination meetings beginning at least two months ahead of planned security go live dates, to coordinate site and space access, space lockdown and other items. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
20 | Security | §C.e | Coordination & Inspections: Meta Security requests to conduct a minimum of two site observations during construction to ensure scope is being executed correctly in accordance with the contract documents. These will generally occur prior to base-build security completion and Meta fit out security completion. Prior to the observations occurring, Meta Security will communicate the dates & associated agendas for each walk at least 30 days prior to it occurring. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
20 | Security | §D.a | Environmental Design and Construction: Telecommunications Vaults | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | See comments to §D.a.i and §D.a.ii, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
20 | Security | §D.a.i | Environmental Design and Construction: All telecommunication vaults, on data center property, shall be located within security perimeter fence line and physically secured by the landlord to prevent unauthorized access (e.g., lockable bolt, lockable cover, padlock) | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
20 | Security | §D.a.ii | Environmental Design and Construction: Subject to Meta review and approval, telecommunication vaults located outside the secure perimeter, shall be locked and alarmed to detect intrusion. | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
20 | Security | §D.b | Environmental Design and Construction: Fence | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | N/A
20 | Security | §D.b.i | Environmental Design and Construction: A secure perimeter around the property shall be provided including a physical barrier to restrict access by pedestrians and vehicles (e.g., fence) and one or more secure entrances to provide vehicle and pedestrian access through the secure perimeter. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
20 | Security | §D.b.ii | Environmental Design and Construction: The fence shall contain no person-passable openings, except those required for any secure entries, and reasonably restrict access by climbing by maintaining a minimum height above grade of 8 feet with an anti-climb topper. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.b.iii | Environmental Design and Construction: The fence shall contain no person-passable openings, except those required for any secure entries, and reasonably restrict access by climbing by maintaining a minimum height above grade of 8 feet with an anti-climb topper. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.c | Environmental Design and Construction: Site Entrance | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | N/A
21 | Security | §D.c.i | Environmental Design and Construction: Secure entries shall allow for verification of business need for all access by personnel, pedestrians or in vehicles prior to permitting access through the secure perimeter. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.c.i | Environmental Design and Construction: Secure entries shall utilize access control and video surveillance systems to document site access and provide a historic record for investigations. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.d | Environmental Design and Construction: Building Requirements | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | N/A
21 | Security | §D.d.i | Environmental Design and Construction: A continuous secure envelope around Meta’s Leased Space including walls, doors, and access points (including below raised floors and above drop ceilings) shall be provided. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.d.ii | Environmental Design and Construction: All Landlord equipment, support spaces, network infrastructure support spaces (e.g., MDF, BDF, etc.), and electrical infrastructure support space shall be physically separated from the Meta’s leased space. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.d.iii | Environmental Design and Construction: The Landlord shall provide secure cages within Meta space to separate General System Racks from Production Racks. Cage design shall be in accordance with Meta’s requirements. | TFO | Comply |  | Secure cages within Meta spaces, if required, will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §D.d.iv | Environmental Design and Construction: Meta’s Production Network gear which performs fabric aggregation functions shall be located within the Network Suite or GS.MDF and be physically separated from the data hall. Meta to advise during design. | TFO | Comply |  | Any work required to physically separate Meta's production network gear from the data hall will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.a | Secured Cage or Mesh Wall Requirements: General | TFO | Comply |  | See comments to §E.a.i, §E.a.ii, and §E.a.iii, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | N/A
21 | Security | §E.a.i | Secured Cage or Mesh Wall Requirements: Secure cages/mesh walls are used to physically partition spaces within data centers to restrict physical access to a space (e.g. IDF, etc.) | TFO | Comply |  | Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.a.ii | Secured Cage or Mesh Wall Requirements: When required, they shall not impede airflow or equipment operation. Impact on airflow and cooling shall be considered in the design. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.a.iii | Secured Cage or Mesh Wall Requirements: Adhere to required clearances to adjacent equipment, exit paths, doorways, rack pathways, and other equipment. | TFO | Comply |  | Landlord will adhere to code-required clearances as part of the Base Build scope-of-work. Accommodation for specific clearances required by Meta will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.b | Secured Cage or Mesh Wall Requirements: Design Requirements | TFO | Comply |  | See comments to §E.b.i, §E.b.ii, §E.b.iii, and §E.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | N/A
21 | Security | §E.b.i | Secured Cage or Mesh Wall Requirements: Secure cages shall be at least 8’ AFF or the height required for rack height, but not higher than tier 3 tray. | TFO | Comply |  | Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.b.ii | Secured Cage or Mesh Wall Requirements: The cage shall be constructed from wire mesh panels attached to posts. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.b.iii | Secured Cage or Mesh Wall Requirements: The maximum gap between the bottom of the mesh panel and the floor below shall be 2 inches. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.b.iv | Secured Cage or Mesh Wall Requirements: If required, provide a screen or fabric attached to mesh for visual privacy. | TFO | Comply |  | Any privacy screens or panels required will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
21 | Security | §E.c | Secured Cage or Mesh Wall Requirements: Material | TFO | Comply |  | See comments to §E.c.i and §E.c.ii, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A | N/A
21 | Security | §E.c.i | Secured Cage or Mesh Wall Requirements: Wire Mesh: 1”x1” powder coated black wire mesh; 9-gauge (minimum) | TFO | Comply |  | Base Building cage or mesh wall wire mesh will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall wire mesh requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any wire mesh for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §E.c.ii | Secured Cage or Mesh Wall Requirements: Posts: 2”x2” post anchored to concrete slab or raised access floor (as applicable). If the cage is on a raised floor, then there is no need to extend below the raised floor. | TFO | Comply |  | Base Building cage or mesh wall support posts will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall support post requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any support posts for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §E.d | Secured Cage or Mesh Wall Requirements: Doors | TFO | Comply |  | See comments to §E.d.i, §E.d.ii, and §E.d.iii, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A | N/A
22 | Security | §E.d.i | Secured Cage or Mesh Wall Requirements: All doors shall be wire-mesh doors with electrified hardware, door actuators, and applicable access control, and door position switch. Strobes and sounders may be installed at the behest of the landlord, Meta Security takes no exception to the installation of these devices. | TFO | Comply |  | Base Building cage or mesh wall doors and access control will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door and access control requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any doors and access control for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §E.d.ii | Secured Cage or Mesh Wall Requirements: Secure cage door hinges shall be located on the interior (secure) side or utilize tamper- resistant hardware. | TFO | Comply |  | Base Building cage or mesh wall door hinges and hardware will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door hinge and hardware requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §E.d.iii | Secured Cage or Mesh Wall Requirements: Secure cage doors shall be designed to prevent manipulation of interior (secure side) hardware from the exterior (unsecure side). A typical method is through incorporating anti-tamper steel sheeting to mitigate the risk of manipulation of door hardware from the non-secure side. | TFO | Comply |  | Base Building cage or mesh wall door hardware and trim will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door hardware and trim requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any door hardware and trim for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §E.e | Secured Cage or Mesh Wall Requirements: Video Surveillance | Base Build (part), TFO (part) | Comply |  | See comments to §E.e.i and §E.e.iii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | N/A
22 | Security | §E.e.i | Secured Cage or Mesh Wall Requirements: Cameras shall provide ID level video coverage at both card readers as per video surveillance requirements section. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance of cage or mesh wall ingress and egress locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta video surveillance requirements for cage or mesh wall ingress and egress locations can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any video surveillance of secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §E.e.ii | Secured Cage or Mesh Wall Requirements: Security cabling shall be contained within the caged area. | Base Build (part), TFO (part) | Comply |  | Base Building security cabling for cage or mesh wall ingress and egress locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta security cabling requirements for cage or mesh wall ingress and egress locations can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any security cabling for cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §F.a | Loading dock: The loading dock shall be considered shared Meta space in which the Landlord will be responsible for providing, managing, and maintaining all aspects of the following security measures within the space, including as a minimum (i) Access Control System, (ii) Video Monitoring System. | Base Build | Comply |  | Base Building access control and video monitoring for the loading dock will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control or video monitoring systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §F.b | Loading dock: There shall be Landlord provided, managed, and maintained overview-level video coverage of the exterior of the loading dock. | Base Build | Comply |  | Base Building video monitoring for the loading dock will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video monitoring systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
22 | Security | §F.c | Loading dock: Meta shall always have reasonable access to a loading dock and a freight elevator at all times (in common with other tenants of the Building), subject to the Building Rules and Regulations. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | Comply | N/A
22 | Security | §F.d | Loading dock: Doors from the exterior into the loading dock shall be secured by the Landlord using 2-factor access control. | Base Build | Comply |  | Landlord's standard Base Building access control from the exterior into the loading dock is via card reader. Two-factor authentication (card-key plus biometric) can will be provided as part of the Tenant Fit-Out (TFO) Base Build scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
22 | Security | §G.a | Access Control: General | Base Build | Comply (part); Deviation (part); Exception (part) |  | See comments to §G.a.i through §G.a.vi, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that security is a Landlord responsibility and will be provided as part of the Base Build. Compliance with, deviation from, or exception to specific requirements in the "Security" will be stated for each individual requirement. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | Jason Brunen
22 | Security | §G.a.i | Access Control: The Landlord shall be responsible for providing, managing, and maintaining all aspects of the access control system for the entire Data Center, including within Meta leased space. This includes all cabling, pathways, rough-in, and devices for all access controlled doors. | Base Build | Comply |  | Base Building access control will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that security is a Landlord responsibility and will be provided as part of the Base Build. Compliance with, deviation from, or exception to specific requirements in the "Security" will be stated for each individual requirement. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Jason Brunen
22 | Security | §G.a.ii | Access Control: All exterior doors into the Data Center shall be access-controlled by the Landlord. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
23 | Security | §G.a.iii | Access Control: The Landlord shall not traverse Meta leased space to access other Landlord space (electrical rooms, etc.) | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
23 | Security | §G.a.iv | Access Control: There shall be no designated path of egress from landlord/common space through Meta leased space, unless unavoidable and required by the AHJ and approved by the Meta. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
23 | Security | §G.a.v | Access Control: There shall be no exterior doors that lead directly into Meta leased space unless unavoidable and required by the AHJ and approved by the Meta. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
23 | Security | §G.a.vi | Access Control: Access control system shall adhere to OSDP version 2.2 or latest version | TFO | Comply (part); Deviation (part); Exception (part) |  | Compliance with, deviation from, or exception to access control system requirements per OSDP version 2.2 or the latest version will be determined as part of Tenant Fit-Out (TFO) scope-of-work. Installation of access control system equipment to support each particular requirement of OSDP version 2.2 or the latest version will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty will review the OSDP version 2.2 requirements with Meta to determine compliance with, deviation from, or exception to specific requirements within the document. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
23 | Security | §G.b | Access Control: Meta Lease Space | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | See comments to §G.b.i through §G.a.ix, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty will review the OSDP version 2.2 requirements with Meta to determine compliance with, deviation from, or exception to specific requirements within the document. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | Dalton Rosenberger
23 | Security | §G.b.i | Access Control: Meta leased space shall be access-controlled using either a multi-factor authentication (2-fac) or single-factor authentication (1-fac) approach. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.ii | Access Control: Multi-factor authentication requires two different types of identify factors to enter: (1) Something you have (e.g., Card, Key, etc.) AND EITHER (2) Something you know (e.g., PIN, Username/Password) or (3) Something you are ( e.g., Fingerprint, Facial Geometry, etc.). | Base Build (part), TFO (part) | Comply |  | Landlord standard multi-factor authentication is card-key plus biometric access control. Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.iii | Access Control: Single-factor identification is used for all access-controlled doors not implementing a multi-factor approach. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.iv | Access Control: The type of access control provided for entry and exit of Meta leased space shall be dictated by the Meta's space type requirements (Refer to Device Matrix). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v | Access Control: 2-factor authentication in and 1-factor authentication out shall be used in spaces that are designated as high-risk and/or critical to the success of the operation (Refer to Device Matrix). These spaces shall be designated by the Meta and include but not limited to: | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v.1 | Access Control: All spaces with access to or are part of the Metas’s network (e.g. MDF, Network Suite, Data Hall, IDF, etc.). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v.2 | Access Control: High-value assets and/or equipment that will transmit or store user data is present (e.g. IBOS storage). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v.3 | Access Control: The doorway is an entry to Meta’s leased space housing core datacenter infrastructure (e.g., Production Network spaces, Data Halls, etc.). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v.4 | Access Control: General controls for the entire building’s facility operations systems are present. This includes but is not limited to spaces in which FacNet network switches or FacNet Client devices are present. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v.5 | Access Control: All doors into ERAD spaces | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.v.6 | Access Control: Controls for the entire building’s security systems are present | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.vi | Access Control: If none of the above 2-factor conditions exist, a minimum of 1 factor of identity authentication shall be provided where one or more of the following conditions exist (Refer to Device Matrix): | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.vi.1 | Access Control: Controls for a portion of the security systems of the building are present | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
23 | Security | §G.b.vi.2 | Access Control: Physical security keys to the building are present. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §G.b.vi.3 | Access Control: Mechanical equipment, electrical equipment, or other controls are present which could impact operations in a portion of the building | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §G.b.vi.4 | Access Control: Spaces which store equipment, spares, and other materials which are critical to data center operations | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §G.b.vii | Access Control: All access-controlled doors shall be actively monitored with an alerting mechanism that sends an alarm to on-site security personnel when unauthorized access is detected. This includes door forced open, door held open, etc. | Base Build (part), TFO (part) | Comply |  | Monitoring for data hall, POP room, electrical room, mechanical gallery, ancillary space, and other access controlled area doors will be provide as part of the Base Building scope-of-work. Monitoring for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cage) doors will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §G.b.viii | Access Control: All doors shall "fail secure" unless required for life safety egress. Doors that must "fail safe" for life safety egress shall have access control installed on the egress side that only acts to shunt the door alarm. | Base Build (part), TFO (part) | Comply |  | Landlord's standard is to have all doors "fail secure" except where required by local code or AHJ's for life safety egress. Data hall, POP room, electrical room, mechanical gallery, ancillary space, and other facility doors will be provide as part of the Base Building scope-of-work. Doors within Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §G.b.ix | Access Control: The access control system shall adhere to OSDP version 2.2 (or latest). Encryption (Secure Channel) shall be enabled and reader tamper alarm monitoring shall be employed. | TFO | Comply (part); Deviation (part); Exception (part) |  | Compliance with, deviation from, or exception to access control system requirements per OSDP version 2.2 or the latest version will be determined as part of Tenant Fit-Out (TFO) scope-of-work. Installation of access control system equipment to support each particular requirement of OSDP version 2.2 or the latest version will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty will review the OSDP version 2.2 requirements with Meta to determine compliance with, deviation from, or exception to specific requirements within the document. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
24 | Security | §A.a | Video Surveillance: General | Base Build (part), TFO (part) | Comply |  | See comments to §A.a.i through §A.a.iii, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A | N/A
24 | Security | §A.a.ii | Video Surveillance: All building exterior entrances/doors shall have Landlord provided identification-level video surveillance coverage to monitor egress and ingress. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §A.a.ii | Video Surveillance: All aspects of video surveillance within and outside Meta leased space shall be provided, managed, and maintained by the Landlord. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §A.a.iii | Video Surveillance: Landlord shall provide identification level coverage (Pix/ft density of at least 50) of access-controlled doors from Landlord space into Meta space and vice versa. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
24 | Security | §A.b | Video Surveillance: Meta Leased Space/Fit-Out | TFO | Comply |  | See comments to §A.b.i through §A.a.vi, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dalton Rosenberger
24 | Security | §A.b.i | Video Surveillance: Meta leased space requires a layered video surveillance approach dependent on conditions within the space. This approach uses three classifications of coverage: (1) Overview level - (greater than 10 pix/ft density), (2) Recognition Level – (greater than 20 pix/ft density), (3) Identification Level – (greater than 50 pix/ft density) | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
24 | Security | §A.b.ii | Video Surveillance: The location, number of cameras, and performance level of each camera within Meta leased space shall be dictated by the Meta's space type requirements. (Refer to Device Matrix) | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
24 | Security | §A.b.iii | Video Surveillance: Overview level coverage shall be provided in spaces that hold high value assets or where work on high value assets is being done. (IBOS, Spoke, ERAD, etc.). These spaces shall have full coverage with no blackout or dead areas. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
24 | Security | §A.b.iv | Video Surveillance: Recognition level coverage (greater than 20 pix/ft density) shall be provided in the Data Hall. Cameras shall provide coverage throughout main aisles. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
24 | Security | §A.b.v | Video Surveillance: ERAD spaces require specific coverage which includes: | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
25 | Security | §A.b.v.1 | Video Surveillance: Identification level coverage of all working stations with a minimum 1 frame per section (FPS) when no motion detected, and 10 FPS when motion is detected. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
25 | Security | §A.b.v.2 | Video Surveillance: Cameras shall work with very low light (night vision mode) and shall have a sensitivity set to 5 percent motion detection. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
25 | Security | §A.b.v.3 | Video Surveillance: Cameras in the ERAD room(s) should be set to continuously record. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
25 | Security | §A.b.vi | Video Surveillance: Any Landlord IDF supporting the video management system for the Meta’s space shall be located outside of the Meta’s leased space. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
25 | Security | §B.a | Intrusion Detection and Resistance: Devices | Base Build | Comply (part); Deviation (part) |  | See comments to §B.a.i through §B.a.iv, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A | N/A
25 | Security | §B.a.i | Intrusion Detection and Resistance: All Meta dedicated spaces with glazed openings within 10ft. (3 m) of grade shall be laminated glass OR be provided with an anti-shatter film that is reviewed and approved by the Meta. | Base Build | Comply |  | Base Building glazing will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Laminated glass or anti-shatter film will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
25 | Security | §B.a.ii | Intrusion Detection and Resistance: Intrusion detection capability shall be provided at all exterior doors (e.g. door held open and door forced open detection) to establish a secure building perimeter layer. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
25 | Security | §B.a.iii | Intrusion Detection and Resistance: Intrusion detection capability shall be provided at all access controlled doors to detect and alert of unauthorized access. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
25 | Security | §B.a.iv | Intrusion Detection and Resistance: The Landlord shall provide intrusion detection devices to monitor all man passable openings (e.g., louvers, hatches, etc.) into Meta leased space that are not physically secured to prevent unauthorized access (e.g., tamper-resistant fasteners, physical locks, etc.). | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | Dalton Rosenberger
25 | Security | §B.b | Intrusion Detection and Resistance: Construction | Base Build (part), TFO (part) | Comply |  | See comments to §B.b.i and §B.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Items for §B.b.ii, below, will be paid for by Meta as part of TFO NRCs. | N/A | N/A
25 | Security | §B.b.i | Intrusion Detection and Resistance: Where other tenants share a wall with Meta’s high-risk spaces, such walls shall extend below the raised access floor to the slab and to the ceiling by means of security grade wire mesh or other industry recognized secure barrier. Further such walls must be alarmed to detect intrusion. | Base Build | Comply |  | No applicable as Meta is the only tenant in the Building. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. This item is not applicable since Meta is the only tenant in the Building. | Comply | N/A
25 | Security | §B.b.ii | Intrusion Detection and Resistance: ERAD room design shall incorporate visual privacy features to prohibit visibility from outside of Meta Space | TFO | Comply |  | Visual privacy features for ERAD room(s) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
25 | Security | §C.a.i | Network Security: Network Access: Any device not owned and approved for use by Meta shall not be connected to any Meta network. (e.g., laptops, computers, cameras, BMS devices, EPMS devices, etc.) | TFO | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | Comply | N/A
25 | Security | §C.b.i | Network Security: Network Interconnections: The Landlord’s, other tenant, or any other network shall not be connected to any Meta network. | TFO | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | Comply | N/A
25 | Security | §C.c.i | Network Security: Network Interconnections: Network equipment, patch panels, interconnections, splice enclosures or telecommunication outlets, other than those owned or operated by Meta, shall not be collocated in a space or room containing those owned or operated by Meta. | Base Build (part), TFO (part) | Deviation |  | Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. |  | Meta | 3 |  | No response received from Meta. Digital Realty confirms that Building POE and POP rooms will be used by Meta, Landlord, and 3rd party telecommunications carriers | Deviate: Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. | Jason Brunen
26 | Security | §C.c.ii | Network Security: Network Interconnections: An exception to the above may be granted by the Meta for spaces where the Meta’s fiber infrastructure is intended to connect to carrier equipment. | Base Build (part), TFO (part) | Deviation |  | Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. |  | Meta | 3 |  | No response received from Meta. Digital Realty confirms that Building POE and POP rooms will be used by Meta, Landlord, and 3rd party telecommunications carriers | Comply | Jason Brunen
26 | Security | §C.c.iii | Network Security: Network Interconnections: All video surveillance and access control devices shall be routed back to the Landlord’s IDF. There shall be no devices that connect to a Meta IDF, this includes devices that are located within the Meta’s leased space. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
26 | Security | §C.c.iv | Network Security: Network Interconnections: All cabling that supports video surveillance and access control shall be physically separated from Meta network cabling. This includes devices that are located within the Meta’s leased space. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | N/A
26 | Security | §C.d.i | Network Security: Telecommunication Pathways and Vaults between Meta-Lease Spaces: Exterior telecommunications pathways used to connect multiple Meta-leased spaces shall be secured and protected from unauthorized access. The Landlord shall be able to detect when those spaces are accessed. | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty has provided costs to modify the OSP vaults, manhole openings, security monitoring, access control, and duct bank conduit quantities. Any modifications to Landlord's baseline installations will be paid for by Meta as part of TFO NRCs. | Comply | Jason Brunen
26 | Security | §C.d.ii | Network Security: Telecommunication Pathways and Vaults between Meta-Lease Spaces: The Landlord shall notify Meta: (1) Before such a space is scheduled to be accessed so that Meta can monitor the network for intrusion, (2) Immediately when unscheduled access to such a space occurs. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | Comply | N/A
26 | Security | §D.a | Device Matrix: High Risk Spaces Includes table listing (11) space types and their associated access control and video surveillance requirements. | Base Build (part), TFO (part) | Comply |  | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
27 | Security | §D.b | Device Matrix: Low/Medium Risk Spaces Includes table listing nine (9) space types and their associated access control and video surveillance requirements. | Base Build (part), TFO (part) | Comply |  | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
27 | Security | §D.Notes | Device Matrix: Notes: • Where there is an interconnecting door between the Network Hub and Megapod, Network Hub shall be 2-fac in, and 1-fac out into the Megapod • There shall be no designated path of egress from the Megapod through the Network Hub unless required by the AHJ and approved by Meta • Where a space requires 2-FAC and shares an interconnecting door with another Meta controlled space, it shall have 1-FAC access control in and out. • When a space requiring 2-fac shares an interconnecting door with another Meta space it shall have 1-factor access control installed on both sides. • Overview level - (greater than 10 pix/ft density), Recognition Level – (greater than 20 pix/ft density), Identification Level (ID) – (greater than 50 pix/ft density) | Base Build (part), TFO (part) | Comply |  | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Comply | Dalton Rosenberger
27 | Connectivity | §E.a | OSP Pathway: Carrier Pathways | Base Build | Comply |  | See comments to §E.a.i through §E.a.iv, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A | N/A
27 | Connectivity | §E.a.i | OSP Pathway: Pathways are to be provided to allow for outside carriers to enter facility from 4 diverse entry points | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
27 | Connectivity | §E.a.ii | OSP Pathway: Require minimum of 25’ separation between 4 diverse pathways | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §E.a.iii | OSP Pathway: Meta requires latitude/longitude to be provided for vault entry points to the campus duct ring. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §E.a.iiv | OSP Pathway: Required to provide outside carriers with location to tie into the campus to provide service | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §E.b | OSP Pathway: Production Pathways | Base Build | Comply |  | See comments to §E.b.i through §E.b.ii, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A | N/A
28 | Connectivity | §E.b.i | OSP Pathway: Pathways are to be provided to interconnect the fiber cabling between buildings 1 through 3 for the back end (BE) and Front End (FE) network. | Base Build | Comply |  | There are only two (2) buildings on the campus. Production pathways will be provided to connect these buildings. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §E.b.i.1 | OSP Pathway: BE Network | Base Build | Comply |  | See comments to §E.b.i.1.a, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A | N/A
28 | Connectivity | §E.b.i.1.a | OSP Pathway: There shall be a requirement of 2 diverse entry points with a required minimum of 25’ separation between the 2 diverse pathways. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §E.b.i.2 | OSP Pathway: FE Network | Base Build | Comply |  | See comments to §E.b.i.2.a, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A | N/A
28 | Connectivity | §E.b.i.2.a | OSP Pathway: There shall be a requirement of 4 diverse entry points with a required minimum of 25’ separation between the 4 diverse pathways. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §E.b.ii | OSP Pathway: Meta requires latitude/longitude to be provided for vault entry points to the campus duct ring. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | N/A
28 | Connectivity | §F | ISP Pathways | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.a. through §F.b.iii.4.b.iv, below. |  | -- | 1 |  | Header item only. | N/A | N/A
28 | Connectivity | §F.a | ISP Pathways: ISP Pathways Supporting OSP | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.a.i through §F.a.ii.5, below. |  | -- | 1 |  | Header item only. | N/A | N/A
28 | Connectivity | §F.a.i | ISP Pathways: ISP Pathways Supporting OSP: Supporting Spaces | TFO | Comply |  | Compliance to requirements will be provided as part of Tenant Fit-Out scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
28 | Connectivity | §F.a.i.1 | ISP Pathways: Refer to the Building Interior and Structure section for space allocation and sizing requirements. | TFO | Comply |  | Compliance to 'Building Interior and Structure' section ISP pathway space quantity and sizing requirements will be provided as part of Tenant Fit-Out scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
28 | Connectivity | §F.a.i.2 | ISP Pathways: Meet Me Room ("MMR") | TFO | Comply |  | See comments to §F.a.i.2.a through §F.a.i.2.c, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
28 | Connectivity | §F.a.i.2.a | ISP Pathways: Each MMR requires 4 racks to be reserved for Meta use. These shall be (4) CPI 4-post racks. Refer to Power section for rack electrical requirements. | TFO | Comply |  | CPI 4-post racks for Meta use and associated electric power circuits will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
28 | Connectivity | §F.a.i.2.b | ISP Pathways: Landlord responsible for coordinating with Meta carriers and providing a provisioned MMR room in accordance with Meta carrier install schedules. | TFO | Comply |  | Landlord will provide a provisioned MMR room as part of the Tenant Fit-Out (TFO) scope-of-work. Carrier install schedules will be as detailed with the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
28 | Connectivity | §F.a.i.2.c | ISP Pathways: Pathways from MMR to Network Suites shall be designed by Meta. Installation of pathways shall be coordinated with Meta during design. | TFO | Comply |  | Pathways from MMR to Network Suites will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
28 | Connectivity | §F.a.ii | ISP Pathways: Entrance Facilities ("EF") | TFO | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.a.ii.1.a through §F.a.ii.5, below. |  | -- | 1 |  | Header item only. | N/A | N/A
28 | Connectivity | §F.a.ii.1 | ISP Pathways: All OSP conduits stubbing up into room to be coordinated with Meta. | Base Build | Exception |  | OSP conduit stub-up locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. |  | Digital Realty | 3 |  | No response received from Meta. Digital Realty confirms that OSP conduit stub up locations will be determined by Landlord. Item will be paid for by Digital Realty as part of Base Build. | Comply | Jason Brunen
28 | Connectivity | §F.a.ii.2 | ISP Pathways: Room walls shall be covered with fire-rated plywood. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Comply | Dan Kingman
28 | Connectivity | §F.a.ii.3 | ISP Pathways: Rooms are to be dedicated to Meta use. | Base Build | Deviation |  | Building entrance rooms (EF, POE, and POP rooms) may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. |  | Meta | 3 |  | No response received from Meta. Digital Realty confirms that Building entrance rooms (Efs, POEs, POP rooms) will be used by Meta, Landlord, and 3rd party telecommunications carriers | Deviate: Building entrance rooms (EF, POE, and POP rooms) may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. | Jason Brunen
28 | Connectivity | §F.a.ii.4 | ISP Pathways: All ladder racks and trays in the room shall be designed and installed by Meta. | TFO | Comply |  | Building entrance rooms (EF, POE, and POP rooms) will have ladder rack and/or fiber tray designed and installed by Landlord as part of the Base Build scope-of-work. Redesign and moves-adds-changes for ladder racks and/or fiber trays can be provided Meta as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Per this requirement, Digital Realty response is changed to "Comply" and we confirm that all ladder racks and trays in Entrance Facilities (EF) shall be designed and installed by Meta | Comply | Dan Kingman
28 | Connectivity | §F.a.ii.5 | ISP Pathways: If the DC is a multistorey facility, the EF room shall also be utilized as a riser for OSP and ISP fiber. LL to provide all associated knockouts and pathways. | Base Build (part), TFO (part) | Comply |  | The building is a two (2) storey facility. Utilization of the building entrance rooms (EF, POE, and POP rooms) as a riser and engineering, furnishing, and installing pathways (and associated knockouts, core drilling, and other penetrations) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b | ISP Pathways: ISP Pathways | TFO | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.b.i through §F.b.iii.4.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
29 | Connectivity | §F.b.i | ISP Pathways: Cabling to support Front End (FE), Back End (BE), and General Systems (GS) shall be supported by ladder tray (Tier-1), Cable Trough (Tier-2), and basket tray (Tier-3, Tier-4, Tier-5, and Tier-GS). These tray tiers shall be implemented as needed to support the connectivity to/between meta network spaces (Network Suites, Megapods, GSIDF, etc.) and landlord spaces (POE and MMRs). | TFO | Comply |  | Ladder tray, cable trough, and basket tray to support Front End (FE), Back End (BE), and General Systems (GS) cabling will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.ii | ISP Pathways: Key Spaces | TFO | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.b.ii.1 through §F.b.ii.4.b, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | N/A | Jason Brunen
29 | Connectivity | §F.b.ii.1 | ISP Pathways: Refer to the Power section for power rating requirements per space. | TFO | Comply |  | Compliance to 'Power' section requirements will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.ii.2 | ISP Pathways: Network Suites | TFO | Exception |  | See comments to §F.b.ii.2.a, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | N/A | Jason Brunen
29 | Connectivity | §F.b.ii.2.a | ISP Pathways: Provide four (4) Network Suites per Region. Network Suites must be able to be connected to each Megapod in the region while maintaining the 25% failure domain requirement. | TFO | Exception |  | Exception is taken to this item as it refers to Meta "Regions" and does not contain any scope-of-work requirements. The number of Network Suites to be provided will be as stated within the Lease. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Comply | Jason Brunen
29 | Connectivity | §F.b.ii.3 | ISP Pathways: Megapods | TFO | Exception |  | See comments to §F.b.ii.3.a and §F.b.ii.3.b, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | N/A | Jason Brunen
29 | Connectivity | §F.b.ii.3.a | ISP Pathways: Each Megapod will contain a Main Distribution Frame (MDF) and dedicated IT rows. The MDF is a network space that provides connectivity between Megapods and Network Suites. | TFO | Exception |  | Exception is taken to this item as does not contain any scope-of-work requirements. The number of Megapods, Main Distribution Frames, and dedicated IT rows to be provided will be as stated within the Lease. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Comply | Jason Brunen
29 | Connectivity | §F.b.ii.3.b | ISP Pathways: Provide a maximum of forty-eight (48) Megapods per Region. | TFO | Exception |  | Exception is taken to this item as it refers to Meta "Regions" and does not contain any scope-of-work requirements. The number of Megapods to be provided will be as stated within the Lease. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Deviate: sixteen (16) Megapods to be provided | Jason Brunen
29 | Connectivity | §F.b.ii.4 | ISP Pathways: Support spaces | TFO | Comply |  | See comments to §F.b.ii.4.a and §F.b.ii.4.b, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
29 | Connectivity | §F.b.ii.4.a | ISP Pathways: Refer to the Building Interior and Structure section for space quantity and sizing requirements. | TFO | Comply |  | Compliance to 'Building Interior and Structure' section ISP pathway space quantity and sizing requirements will be provided as part of Tenant Fit-Out scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.ii.4.b | ISP Pathways: Refer to the Power section for power rating requirements per space. | TFO | Comply |  | Compliance to 'Power' section requirements will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.iii | ISP Pathways: GS Spaces | TFO | Comply |  | See comments to §F.b.iii.1 through §F.b.iii.4.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
29 | Connectivity | §F.b.iii.1 | ISP Pathways: GSIDF | TFO | Comply |  | See comments to §F.b.iii.1.a through §F.b.iii.1.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
29 | Connectivity | §F.b.iii.1.a | ISP Pathways: Meta uses the standard of determining GSIDF coverage using a diamond centered at the center of the IDF with a diagonal from the center of the diamond to a corner of the diamond with 235’ in length. Anything within the diamond is considered covered by the GSIDF. GSIDFs coverage must contain all Network Suites, Megapods, and common spaces completely. If coverage exceptions are needed, these will require Meta approval. | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.iii.1.b | ISP Pathways: Number of rack positions - 2 | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.iii.1.b.i | ISP Pathways: Rack 01 passive and Rack 02 active. | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.iii.1.b.i | ISP Pathways: iCPI 4-post for all racks | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
29 | Connectivity | §F.b.iii.2 | ISP Pathways: ADMIDF | TFO | Comply |  | See comments to §F.b.iii.2.a through §F.b.iii.2.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
29 | Connectivity | §F.b.iii.2.a | ISP Pathways: ADMIDF coverage is determined in a similar manner as GSIDFs utilizing the diamond coverage method. ADMIDF coverage must include all admin/office space for the floor the IDF is on. ADMIDF coverage is limited to the floor on which the ADMIDF is on. If coverage exceptions are needed, these will require Meta approval. | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.2.b | ISP Pathways: Number of rack positions – 4 | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.2.b.i | ISP Pathways: 2 active (Rack positions 02, 03) and 2 passive (Rack positions 01, 04). | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.2.b.ii | ISP Pathways: CPI 4-post for all racks | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.3 | ISP Pathways: GSMDF | TFO | Comply |  | See comments to §F.b.iii.3.a through §F.b.iii.3.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
30 | Connectivity | §F.b.iii.3.a | ISP Pathways: Co-located in each Network Suite, Rows 01 and 02. | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.3.b | ISP Pathways: Number of rows in each space - 2 | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.3.b.i | ISP Pathways: Number of rack positions in each row – 23 (Racks 01-03; 21-23 passive; Racks 04-20 active). | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.3.b.ii | ISP Pathways: CPI 4-post for Active Racks and CPI 2-post for Passive Racks. | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.4 | ISP Pathways: Riser Rooms | TFO | Comply |  | See comments to §F.b.iii.4.a through §F.b.iii.3.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A | Dan Kingman
30 | Connectivity | §F.b.iii.4.a | ISP Pathways: For carrier and inter-building front-end connectivity, if multi-story building four risers are required to connect MDF spaces across floors. This is achieved by utilizing 4” conduit sleeves. Meta to coordinate the quantity of knockouts required. | TFO | Comply |  | The building is a two (2) storey facility. Engineering, furnishing, and installing risers, riser pathways, and associated conduit sleeves, knockouts, core drilling, and other penetrations will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.4.b | ISP Pathways: For intra-building back-end network connectivity, risers shall be placed between back-end MDF pairs. | TFO | Comply |  | The building is a two (2) storey facility. Engineering, furnishing, and installing risers, riser pathways, and associated conduit sleeves, knockouts, core drilling, and other penetrations will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.i | ISP Pathways: Riser configuration and slot dimension to be coordinated with Meta. | TFO | Comply |  | Riser configuration, penetration sizing & dimensions, and coordination with Meta will be determined and provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.ii | ISP Pathways: Preferred dimension 20”x 6” with 6 FT minimum between slots | TFO | Comply |  | Riser configuration, penetration sizing & dimensions, and distance between penetrations will be determined as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.iii | ISP Pathways: If perforations are located within accessible spaces, these must be secured in compliance with safety requirements. | TFO | Comply |  | Riser penetration locations, penetration accessability, and health & safety considerations will be addressed as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.iv | ISP Pathways: Location and sizing of penetration zones for ISP pathways shall be coordinated with Meta for clash detection with other systems. | TFO | Comply |  | Riser configuration, penetration sizing & dimensions, and coordination with Meta will be determined and provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
30 | Connectivity | §G | Cabling | TFO | Exception |  | See comments to §G.a through §G.f.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta |  | N/A
30 | Connectivity | §G.a | Cabling: All Cabling shall be designed and installed by Meta to meet the network requirements set by pINE and ENS. Cabling design is broken down by use case below and includes any outside plant (OSP), inside plant (ISP) and patch cabling. | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
30 | Connectivity | §G.b | Cabling: Carrier | TFO | Exception |  | See comments to §G.b.i through §G.b.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta |  | N/A
30 | Connectivity | §G.b.i | Cabling: Outside Carrier to bring in new service via fiber optic cable to POE and/or MMR to provide lit and dark service for the Meta network | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
30 | Connectivity | §G.b.ii | Cabling: Services Handed off in the POE will tie to a house Meta Carrier cable which will be designed and routed by Meta on Tier-GS from POE to Network Suites. Cabling from a POE shall remain diverse from other POEs going to the same Network Suite. POE shall provide 4 diverse paths to each Network Suite. | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.b.iii | Cabling: Services Handed off in the MMR will tie to a house Meta Carrier cable which will be designed and routed by Meta on Tier-GS from MMR to Network Suites. Cabling from an MMR shall remain diverse from other MMRs going to the same Network Suite. MMRs shall provide a path to each Network Suite to be diverse from any other (minimum of 2 MMR for region) | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.c | Cabling: General Systems (GS) | TFO | Exception |  | See comments to §G.c.i through §G.c.v, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta |  | N/A
31 | Connectivity | §G.c.i | Cabling: 2 Network Suites will serve as the main GSMDFs for the region. GS will be a 2- path system for the region, where path 1 comes from one Network Suite and path 2 comes from the other | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.c.ii | Cabling: GS cabling shall be provided between Network Suites | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.c.iii | Cabling: All GSIDF and ADMINIDF shall be numbered in accordance with coordination with ENS | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.c.iv | Cabling: PTP Cabling shall connect to each Network suite providing 4 distinct paths for cabling | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.c.v | Cabling: MGMT and Console Fiber cabling shall be designed to support the production network (Front-End and Back-End) | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.d | Cabling: CorpNet | TFO | Exception |  | See comments to §G.d.i through §G.d.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta |  | N/A
31 | Connectivity | §G.d.i | Cabling: All AP layouts shall be designed by Meta-RSE and installed by DEC managed vendors. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.d.ii | Cabling: Overall floorplans, clearly indicating Meta-Exclusive Occupied space for AP layout and integration into Technology Drawing Sets. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.d.ii.1 | Cabling: The “Overall AP Layout Plan” should show walls, doors, cable tray as full-tone and racks, HAC, shelving and room names as half-tone. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.d.ii.2 | Cabling: Once the Overall Plans are provided to the RSE TDM they will send back AP Layouts to be included by the TEOR into the drawings set. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.d.iii | Cabling: In addition the Overall AP Layout Plan will be AP mounting details for all AP mounting types occurring within the space. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts or mounting details into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.e | Cabling: Front-End (FE) | TFO | Exception |  | See comments to §G.e.i through §G.e.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta |  | N/A
31 | Connectivity | §G.e.i | Cabling: All Cabling required to connect layers in Network Suites, between Network Suites, and from Network Suites to Megapods | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.e.ii | Cabling: Designed as 4 diverse paths system between network topology layers | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.e.iii | Cabling: Leverages outside designated goalpost in Megapods | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.f | Cabling: Back-End (BE) | TFO | Exception |  | See comments to §G.f.i through §G.f.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta |  | N/A
31 | Connectivity | §G.f.i | Cabling: All Cabling required to connect layers between Megapods by either direct cabling between megapods and/or cabling from Megapods to Network Suites | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.f.ii | Cabling: Designed as 2 diverse path system between network topology layers | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
31 | Connectivity | §G.f.iii | Cabling: Leverages inside designated goalpost in Megapods | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | Exception: all cabling shall be designed, furnished, and installed by Meta or others. | N/A
32 | N/A | N/A | Interior lighting controls sequence of operations Table at top of page #32 | Base Build | Exception |  | Exception is taken to the "Interior Lighting Controls Sequence Of Operations" table at the top of page #32. Lighting controls and lighting controls sequence of operations (SOO) will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. |  |  | 3 |  |  | Comply | Jason Brunen
32 | DAS/PTP | §A | Public Safety (ERRCS) DAS | Base Build | Deviation |  | See comments to §A.a through §A.a.iv, below. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. |  | Dan Kingman
32 | DAS/PTP | §A.a | Public Safety (ERRCS) DAS: Provide a Public Safety DAS system to comply with building and fire code requirements and to ensure first responder radio coverage is provided. | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §A.a.i | Public Safety (ERRCS) DAS: OEM: ADRF or Zinwave | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §A.a.ii | Public Safety (ERRCS) DAS: Active equipment to be UL2524 compliant | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §A.a.iii | Public Safety (ERRCS) DAS: Coordinate with local AHJ on required local frequencies/channels | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §A.a.iv | Public Safety (ERRCS) DAS: Coordinate rooftop antenna location to ensure donor signal functionality | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §B | Land Mobile Radio (LMR - Handheld radio) System | TFO | Comply |  | See comments to §B.a through §B.c, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §B.a | Land Mobile Radio (LMR - Handheld radio) System: Provide Meta personnel used handheld radio system | TFO | Comply |  | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §B.b | Land Mobile Radio (LMR - Handheld radio) System: LMR system may share infrastructure with PS DAS with AHJ approval | TFO | Comply |  | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
32 | DAS/PTP | §B.c | Land Mobile Radio (LMR - Handheld radio) System: OEM: Motorola | TFO | Comply |  | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §C | Commercial (Cellular) DAS | Base Build (part), TFO (part) | Deviation |  | See comments to §C.a through §C.c, below. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. |  | Dan Kingman
33 | DAS/PTP | §C.a | Commercial (Cellular) DAS: Provide a cellular DAS solution to ensure in-building cell coverage is adequate and also meets e911 requirements. | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §C.b | Commercial (Cellular) DAS: Landlord to obtain their own signal source from carriers (AT&T, Verizon, T-mobile) | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §C.b.i | Commercial (Cellular) DAS: Recommend over-the-air as temporary and fiber base station installed as permanent | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §C.b.ii | Commercial (Cellular) DAS: Provide a timing source (GPS) to support carrier base stations | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §C.c | Commercial (Cellular) DAS: OEMs: Commscope, Solid, ADRF, Corning | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D | Precision-Timing-Protocol (GPS) | TFO | Comply |  | A Precision-Timing-Protocol (GPS) system will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.a | Precision-Timing-Protocol (GPS): Landlord to provide PTP pathway/infrastructure to accommodate 4 (four) PTP antennas | TFO | Comply |  | A Precision-Timing-Protocol (GPS) system with pathway/infrastructure to support four (4) PTP antennas will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.b | Precision-Timing-Protocol (GPS): Each PTP antenna is provided by Meta with a pre-terminated cable length attached. Coordinate length with Meta. The antenna OEN is Huber Suhner GPS over fiber. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.c | Precision-Timing-Protocol (GPS): Generally, the PTP antennas terminate to support each network suite (MDF), and coordinate final rack locations with Meta. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d | Precision-Timing-Protocol (GPS): Landlord to provide two-inch or greater roof penetration with an independent pathway for each network suite | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.i | Precision-Timing-Protocol (GPS): A two-inch mast pipe to mount each antenna | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.ii | Precision-Timing-Protocol (GPS): Cable Containment from the antenna mast to the roof penetration | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.iii | Precision-Timing-Protocol (GPS): Continuous pathway from roof penetration to spaces dedicated for meta use | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.iv | Precision-Timing-Protocol (GPS): All cable pathways must maintain a bend radius of greater than 6 inches | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.v | Precision-Timing-Protocol (GPS): Antennas must be mounted below the nearest lightning arresting air terminal | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.vi | Precision-Timing-Protocol (GPS): At the minimum, a 180-degree view of the southern sky is required | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.vii | Precision-Timing-Protocol (GPS): No obstructions should be within a ten-degree angle from the horizon | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.d.viii | Precision-Timing-Protocol (GPS): The antenna mast should be 6 feet away from metallic reflectors | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
33 | DAS/PTP | §D.e | Precision-Timing-Protocol (GPS): Due to the class-4 lasers contained within the PTP system, Laser Warning signs should be incorporated into the design of PTP antenna locations | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Comply | Dan Kingman
[12 empty] | Comply Count | 329
[12 empty] | Deviate Count | 13
[12 empty] | Exception Count | 24
Note on N65: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unless Meta agrees to pay for additional FWUs to decrease to 22FdT
Note on N66: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Unless Meta agrees to pay for additional FWUs to increase to 158 CFM/kW requirement

## D
Page # reference | Section | Subsection | Requirement | Scope | CDE | Landlord comment | Meta Response | DLR / SE Proprosed Stance | Responsible Party | Needs Attention
11 | Architectural | §A.2.ii.a | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Wall mounted objects (fire extinguishers, AEDs, etc) must be clear of the AGV path. | Base Build | Exception | Wall mounted objects (fire extinguishers, AEDs, etc.) may protrude into the corridor. | Will these objected be outside of the 8' clear zone? If so, ok. If they protrude into the 8' zone then not accepted. | [KOB] To the best of our ability, all corridor and pathway wall mounted objects shall be in flush mounted enclosures at Meta's expense
11 | Architectural | §A.2.ii.b | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Where possible, wall mounted objects should be consolidated on one side of the hallway. | Base Build | Exception | Wall mounted objects will be present on both sides of the corridor. | Will these objected be outside of the 8' clear zone? If so, ok. If they protrude into the 8' zone then not accepted. | [KOB] To the best of our ability, all corridor and pathway wall mounted objects shall be in flush mounted enclosures at Meta's expense
7 | Electrical | §B.e.i | Grounding: Provide (2) ground bars in each data hall. Refer to technology for requirements. | Base Build | Deviation | A minimum of two (2) ground bars will be provided in each data hall. Ground bar size, configuration, and locations shall be as stated in Landlord's electrical drawings and specifications. | Will need to be coordinated with technology during TFO to ensure it meets requirements. | Ground bar locations will be shown in construction doucments which will be shared with Meta for their approval during the construction process already addressed in the TFO and lease process.
8 | Electrical | §C.b.i | Network System Grounding: Provide (2) ground bars in each space. Refer to technology for requirements. | Base Build | Deviation | A minimum of two (2) ground bars will be provided in each data hall. Ground bar size, configuration, and locations shall be as stated in Landlord's electrical drawings and specifications. | Will need to be coordinated with technology during TFO to ensure it meets requirements. | Ground bar locations will be shown in construction doucments which will be shared with Meta for their approval during the construction process already addressed in the TFO and lease process.
12 | Architectural | §A.2.iv.f | Programming & Circulation, Corridors and Pathway, Freight Elevators: Provide wall-mirrors around elevators as a safety measure due to heavy PIV/pedestrian traffic and blind corners | TFO | Deviate | Wall mirrors can be provided as part of Tenant Fit-Out (TFO) scope of work. | Why is this called out as a deviation? | We do not install by default, but can install per Meta's request and cost.
7 | Electrical | §B.c.ii | UPS-Backed Ancillary Power: Provide dual 230V, 20A/1P, UPS backed circuits from diverse panels to cold aisle goal post receptacles. | TFO | Deviation | Dual 230V, 20A, 1P, UPS backed circuits from diverse panels will be provided to aisle goal post receptacles as part of Tenant Fit-Out (TFO) scope of work. Hot aisle containment (HAC) will be utilized in all data halls. | Why does this say DEVIATE? Should be comply. | [KOB] Comply.
10 | Mechanical | §C.4 | Data Hall (Megapod)/Network Rooms: The 100 percent/80 percent air-cooling/liquid-cooling infrastructure refers to cooling distribution systems inside the data halls (megapods) and network suites. Note that cooling demand can vary in any combination of 0 to 100 percent air-cooling and 0 to 80 percent liquid-cooling. | Base Build (part); TFO (part) | Comply (part); Deviation (part) | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Same as item 9
10 | Mechanical | §C.3 | Data Hall (Megapod)/Network Rooms: Any space noted as back end network suites shall mirror the data hall requirements. | Base Build (part); TFO (part) | Comply (part); Deviation (part) | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Same as above.
11 | Mechanical | §D.2.iv | Rack-level airside requirements: 0.158 CFM / W [0.075 CMS / W] air flow rate. | Base Build | Deviation | Airside SLAs will be as stated in Exhibit H of the Lease. Base Building design is 147 cfm/kW. | Related to item above. | [KOB] Request submitted to D&C
6 | §3 | N/A | Related Documents: Meta PQM Performance Spec Rev 4 | TFO | Comply (part); Deviation (part); Exception (part) | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. Compliance with, deviation from, or exception to "Meta PQM Performance Spec Rev 4" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | PQM coordination can be part of TFO but expectation is LL is complying with spec.
6 | Electrical | §A | Equipment metering a. Provide CT's, Branch Circuit Monitoring and Meter Enclosures as required per Meta PQM Performance Spec requirements (metering locations to be reviewed/finalized during tenant fit out design development). i. Metering locations to include: 1. Both Normal & Gen power, OR aggregate at all MSB's. 2. Metering of the common bus at all CDP/COD boards. 3. CDP/COD reserve loop feeder breaker in MSB Reserve board . 4. Row-level branch circuit monitoring. b. Provide all required interconnects between meter enclosures and LL equipment as well as Meta gateways (DCIM head end panels). Provide dual 120V UPS backed circuits to all meter enclosures. Refer to the BMS/DCIM section of this document for additional requirements. | TFO | Comply (part); Deviation (part); Exception (part) | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. Compliance with, deviation from, or exception to "Meta PQM Performance Spec Rev 4" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | PQM coordination can be part of TFO but expectation is LL is complying with spec.
6 | Electrical | §B.a.iii | Data Hall Server Row Power: (1) Baseline Tap Box with dual L22-30R per rack position. Tap box layout to be reviewed/finalized during tenant fit out design development. | TFO | Comply | Tap-off box configuration, quantities, and locations will be determined as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Agree
7 | Electrical | §B.a.iv | Data Hall Server Row Power: Maximum available fault current to be 25KAIC at the server PSU input. Where 25KAIC is not achievable, Current-limiting fuse tap boxes must be used. | TFO | Comply | Tap-off box configuration, quantities, and locations will be engineered, furnished, and installed (EF&I) as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Agree
8 | Electrical | §C.a.iv | Network System Row Power: Tapboxes with dual L22-30R per rack position. Tap box type to match server areas. Quantities and locations per rack layout. | TFO | Comply | Tap-off box configuration, quantities, and locations will be determined as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Agree
14 | Architectural | §E.2 | Building Opening & Hardware: Where vision panels are called out in design standards for doors, vision panels shall only be provided in interior Meta spaces, no vision panels in shared spaces. | Base Build | Deviation | Certain common area spaces, such as conference rooms, breakout rooms, and break rooms, have doors with vision panels or glass doors and walls. | Please further clarify deviation.
11 | Architectural | §A.2.ii.c | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Should be clear of temporary obstructions (door swings into corridors, temporary laydown storage, etc.). | Base Build | Exception | Doors will swing out into the corridors. | Ok. Safety signage will need to added in the area of door swing zone.
12 | Architectural | §A.2.ii.e | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: If doors swing into the corridor, the corridor should be widened to allow for 8’-0” clear with the door open. | Base Build | Exception | Corridor widths are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Corridor widths are fixed and cannot be widened. | Ok. Safety signage will need to added in the area of door swing zone.
9 | Mechanical | §C.1 | Data Hall (Megapod)/Network Rooms: Provide infrastructure to support up to 100 percent (by power) air-cooling and up to an average of 80 percent (by power) liquid-cooling at the data hall level. At the individual row level technical water loops shall be sized to support 100 percent (by power) of the electrical busway capacity. | Base Build (part); TFO (part) | Comply (part); Deviation (part) | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Noted that this has been agreed with the leasing team.
5 | §2 | Bullet #1 | Landlord Design Team Expectations: Landlord shall deliver mechanical, electrical, BMS/controls, plumbing, fire protection, architectural, structural, AV, and food services design and construction administration services for the fit-out of data halls, network suites, administration, and support spaces within colocation data center facilities. | Base Build (part); TFO (part) | Comply (part); Exception (part) | Design services and construction administration for certain aspects of mechanical, electrical, BMS/controls, plumbing, fire protection, architectural, and structural systems will be provided as part of Tenant Fit-Out (TFO) scope of work. All design services and construction administration for AV (audio visual) systems will be provided as part of Tenant Fit-Out (TFO) scope of work. Food services design, build-out, and construction administration services will not be provided by Landlord. | Not accepted. We will need to have a microkitchen put in the admin space.
5 | §2 | Bullet #2 | Landlord Design Team Expectations: Landlord Design team is required to contract or coordinate with the following partners for scopes as indicated. | TFO | Comply (part); Exception (part) | Comply with coordinating directly with Meta for cabling; exception is taken to contracting or coordinating with RAS - Ronald Sadusky as food services design, build-out, and construction services will not be provided by Landlord; comply with contracting or coordinating with one of Meta's listed A/V consultants. | Not accepted. We will need to have a microkitchen put in the admin space.
16 | Architectural | §G.2.ii | Interior Construction & Materials, Ceiling: All areas containing food service (FS) equipment must have a finished ceiling installed overhead | Base Build | Exception | Food services design, build-out, and construction administration services will not be provided by Landlord. | Not accepted. We will need to have a microkitchen put in the admin space.
14 | Architectural | §E.1.ii | Building Opening & Hardware, Door Hardware: Refer to the GDSS document for access control requirements. Meta security team to review for compliance with GDSS | Base Build (part), TFO (part) | Deviation | Access control will be as detailed and shown in the Landlord's security drawings, plans, and specifications and will follow the Landlord's standards. Modifications to access control can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Security design must adhere to Meta requirements as outlined in the PDC.
13 | Architectural | §C.4 | Room Numbering: Ensure all spaces, including but not limited to the landlord owned spaces, are numbered, including roof areas. | Base Build | Comply | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Meta may label the rooms per a nomenclautre they accept at their sole cost as part of the TFO process
13 | Architectural | §C.1 | Room Numbering: All Meta dedicated rooms shall adhere to Meta Room Naming and Numbering Standards. | Base Build | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.2 | Room Numbering: If the landlord room numbering follows a different convention, both room numbers shall be provided on the drawings. | Base Build | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.3 | Room Numbering: Room numbers shall follow the guidance in the Meta Data Center Design Room Naming Standards. | Base Build | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.5 | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards. | Base Build | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.5.i | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Meta-Owned MMR rooms shall be named MOMMR followed by a two digit designator. The MOMMR planned to route Path A/B (post 1) shall be MOMMR01 and the MOMMR planned to route Path C/D (post 2) shall be MOMMR02 | Base Build (part), TFO (part) | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.5.ii | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Point of Entry rooms shall be named POE followed by a two digit designator. POEs adjacent to MOMMRs shall share the same two digit designator as the MOMMR. | Base Build (part), TFO (part) | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.5.iii | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Riser rooms shall be named RISER followed by a two digit designator. If the riser is included in the same room as an MOMMR or IDF room than the room shall use the MOMMR or IDF naming convention. The RISER planned to route Post 1 shall be named RISER01, and the RISER planned to route Post 2 shall be named RISER02. | Base Build (part), TFO (part) | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
13 | Architectural | §C.5.iv | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Admin IDF rooms shall be named ADMINIDF followed by a two digit designator. | Base Build (part), TFO (part) | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
14 | Architectural | §C.5.iv | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: General Service IDF rooms shall be named GSIDF followed by a two digit designator. | Base Build (part), TFO (part) | Deviation | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
14 | Architectural | §C.6 | Room Numbering: Ensure corridors are broken up as required to give each segment or turn a unique number. | Base Build | Exception | Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
14 | Architectural | §D.1 | Room Signage: Room signage shall comply with all code and local AHJ requirements. Room signage shall contain both landlord and Meta room numbering if different than Meta standard for all Meta leased spaces. | Base Build (part), TFO (part) | Deviation | Room signage will comply with all code and local AHJ requirements and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
14 | Architectural | §D.2 | Room Signage: META signage (placards) will only be used on all META occupied spaces and these additional landlord spaces: i. Electrical Rooms ii. UPS Rooms iii. Mechanical Galleries iv. House UPS Rooms | Base Build (part), TFO (part) | Deviation | Room signage will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards.
6 | §3 | N/A | Related Documents: Data Center Signage Guidelines | TFO | Comply (part); Deviation (part); Exception (part) | Any and all signage required by Meta to conform to Meta "Data Center Signage Guidelines" requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Meta "Data Center Signage Guidelines" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Need alignment that Meta standards will be followed for Meta occupied spaces.
6 | §3 | N/A | Related Documents: Data Center Space Standards | Base Build | Exception | A general exception is take to Meta "Data Center Space Standards" requirements. Landlord is providing and Tenant is leasing data halls, office space, storage space, and ancillary space(s) based upon Landlord's building design and space planning requirements. | Not accepted. Meta has specific requirements for operating the tenant spaces, and need those to be fit-out per our standards.
11 | Architectural | §A.2.i | Programming & Circulation, Corridors and Pathway: Network Suites and Data Halls shall have an identified path of travel from the loading dock in which all building elements along the path can support the movement of Meta specified server racks and robotic tugs (Autonomour Guided Vehicles, or “AGV”) . Wall mounted objects (fire extinguishers, AEDs, etc) must be clear of the AGV path. | Base Build | Exception | A designated path-of-travel from the loading dock to the network suites and data halls will be established. Corridor width along the path-of-travel will be 8'-0" or greater. Doorway openings along the path-of-travel will be 6'-0" or greater. Certain wall mounted objects (fire extinguishers, AEDs, etc.) may protrude into the corridor and doors may swing out into the corridor. | Not accepted. Doorways along path of rack moves must be 8' wide by 9' high min.
14 | Architectural | §E.3.ii | Building Opening & Hardware, Doors: Doors shall open the maximum extent possible and shall be double doors 8’-0” x 9'-0”. | Base Build | Deviation | Double doors along the rack path are 6'-0" wide x 9'-0" high and will open to the maximum extent possible. | Not accepted. Doorways along path of rack moves must be 8' wide by 9' high min.
14 | Architectural | §E.1.i | Building Opening & Hardware, Door Hardware: Refer to Meta Data Center Requirements (2.1.3 Building Opening Planning & Guidelines) | Base Build (part), TFO (part) | Deviation | Door hardware will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements.
14 | Architectural | §E.3.i | Building Opening & Hardware, Doors: All doors along the rack path shall receive automatic operator and security hardware. | Base Build (part), TFO (part) | Deviation | Doors along the rack path are manually operated and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door operation and hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements.
14 | Architectural | §E.3.ii.a | Building Opening & Hardware, Doors: Controlled double doors into equipment rooms required for movement of loaded racks from docks for installation in equipment areas with adequate clearance to safely maneuver by the robotic tugs. | Base Build (part), TFO (part) | Deviation | Doors along the rack path are manually operated and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door operation and hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors, adequate clearances, and proper door operation (opening) prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements.
14 | Architectural | §E.3.iii.e | Building Opening & Hardware, Doors, Door Hardware: All lock cylinders shall be MEDECO High Security | Base Build (part), TFO (part) | Deviate | Door hardware and lock cylinders will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware and lock cylinders can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements.
15 | Architectural | §E.3.iii.l | Building Opening & Hardware, Doors, Door Hardware: Panic hardware: as required by code and at electrical rooms | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Panic hardware will be provided and installed as required by code. Door hardware will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements.
15 | Architectural | §E.3.iii.m | Building Opening & Hardware, Doors, Door Hardware: All doors to receive REX unless otherwise indicated | Base Build (part), TFO (part) | Deviation | Door functionality allows for free egress at all times. Modifications to door functionality can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements.
10 | Mechanical | §C.2 | Data Hall (Megapod)/Network Rooms: Front end network suites to be 100 percent (by power) air cooled day 1. Liquid cooling requirements for Front end network suites can be a deferred scope including CDU’s and piping. | Base Build (part); TFO (part) | Comply | Infrastructure to support up to 100% (by power) air-cooling at the data hall level will be provided for data halls designated as "Front End Network" data halls as part of the Base Building scope of work. Liquid cooling infrastructure within the data halls, including piping, for data halls designated as "Front End Network" data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. | Not a deviation but the liquid cooling for the FE space can be deferred, is there any benefit to deferring it or is it better to install now? | Decision can be made during the TFO process. All suites are 80/85 liquid and air heat rejection.
11 | Mechanical | §D.2.iii | Rack-level airside requirements: 22°F ΔT [12.2°C ΔT] airside rack ΔT. | Base Build | Deviation | Airside SLAs will be as stated in Exhibit H of the Lease. Base Building design is 23°F ΔT. | Confirm what the impact would be of changing this to be 22F DT. ROM cost or schedule impact.
11 | Mechanical | §D.3.ii | Cooling distribution units (CDUs): UPS support for CDU’s is required. UPS time duration to match server shutdown time. This shall be 90 seconds or as required through discussions with the Meta server hardware team. | Base Build | Deviate | Waterside SLAs will be as stated in Exhibit H of the Lease. Mechanical UPS sizing and ride-through time are as required for Generator restart duration. | CDU UPS must be 5 minute minimum.
12 | Architectural | §A.2.ii.d | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: If the corridor clear width is temporarily obstructed, operations must ensure an 8’-0” clear corridor during rack movements. | Base Build | Exception | It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors and adequate clearances prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Agree
12 | Architectural | §A.2.iii | Programming & Circulation, Corridors and Pathway, AGV Types | Base Build | Exception | It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors and adequate clearances prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Agree
12 | Architectural | §A.2.iv.c | Programming & Circulation, Corridors and Pathway, Freight Elevators: 15,000lbs. Weight capacity | Base Build | Deviation | Freight elevator weight capacity is 12,000 lbs. | Accepted. Confirm elevator is C rated.
5 | §2 | Bullet #3 | Landlord Design Team Expectations: The Landlord is required to provide documents for Meta reviews at 100%SD, 100%DD, 50%CD, and 95%CD. Review sessions shall be open for 5 business days to allow Meta team to comment. All comments shall be adjudicated by the Design Team and provided back to the Meta Team. The Deliverable Requirements Table for Meta fit-out scope is provided as a reference. | Base Build (part); TFO (part) | Comply (part); Exception (part) | Landlord will provide 95%CD or IFC (Issued for Construction) drawings for Base Build items for Tenant review. Exception is taken to providing 100%SD, 100%DD, and 50%CD drawings to Tenant as these milestones have already been completed prior to the Effective Date of the Lease. Landlord will provide 100%SD, 100%DD, 50%CD, and 95%CD drawings for Tenant Fit-Out (TFO) scope of work items as part of Tenant Fit-Out (TFO) scope of work. | Accepted
12 | Architectural | §A.2.iv.a | Programming & Circulation, Corridors and Pathway, Freight Elevators: Located Centrally to IT Equipment Rooms and Loading Dock as possible. | Base Build | Deviation | Freight elevator locations are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Freight elevator locations are fixed and cannot be moved. | Accepted
12 | Architectural | §A.2.iv.e | Programming & Circulation, Corridors and Pathway, Freight Elevators: Interior cab dimensions min: 8’-4” width x 20-’10” depth and 9’-6” height. | Base Build | Deviation | Freight elevator cab depth is 9'-6" width x 10'-6" depth x 10'-0" height | Accepted
15 | Architectural | §F | Meta Lighting Requirements: Includes table listing (19) space types and their associated illimination requirements. | Base Build (part), TFO (part) | Deviation | Landlord is providing a baseline lighting design for all spaces as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted
15 | Architectural | §G.1 | Interior Construction & Materials: Interior partitions shall receive code required fire and smoke wall ratings in addition to minimum 1-hour fire and smoke rated construction between the computer equipment rooms and office areas, between computer equipment rooms and electrical rooms, and around MPOE/BDF rooms, except where greater rating is required by code. | Base Build (part); TFO (part) | Deviation | Interior partitions are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Changes or reconfigurations, including changes in fire ratings, to interior partitions will be provided as part of Tenant Fit-Out (TFO) scope of work, if feasible. All partitions for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted
16 | Architectural | §G.1.i | Interior Construction & Materials: See Meta Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines) | Base Build (part); TFO (part) | Deviation | Materials and acoustic properties are as detailed and shown in the Landlord's architectural drawings, plans, specifications, and basis of design. Changes in materials, acoustic properties, or compliance with Meta "Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines)" will be provided as part of Tenant Fit-Out (TFO) scope of work, if feasible. All materials, acoustic properties, and compliance with Meta "Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines)" for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted
16 | Architectural | §G.2.i | Interior Construction & Materials, Ceiling: A structural ceiling system shall be provided in all data halls and network rooms meeting the loading requirements. The strut ceiling grid shall be braced to control sway from interior air flow and floats around the perimeter to avoid transferring forces into interior or exterior partitions. | Base Build (part), TFO (part) | Deviate | Base building Structural Ceiling Grid to be provided. Meta required hanging loads to be analyzed and modified as required as part of the Tenant Fit-Out (TFO) scope of work. | Accepted
19 | Controls & DCIM | §C.5.iv.a | Mechanical Monitoring - DCIM: The CDUs shall be monitored and controlled (where applicable) by the landlords BMS. | TFO | Comply (part); Deviation (part) | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. The Landlord BMS will monitor and report on CDU operation; however, CDU control will be via separate controllers and control network (top-level Landlord BMS is 'observe and report' only). | [BW] Please confirm control of CDU is done by the landlord regardless if it's a separate controller and/or network. Meta will not be controlling the CDUs.
17 | Controls & DCIM | §C.1 | Meta FacNet and Data Center Infrastructure Management (DCIM): Integration with Meta's DCIM system will involve monitoring all specified electrical parameters to meet both Dynamo and line of demarcation requirements. Additionally, it will monitor critical environmental conditions within essential spaces to ensure compliance with Service Level Agreements (SLAs). | TFO | Comply (part); Deviation (part); Exception (part) | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to monitoring all specified electrical parameters to meet Dynamo and line of demarcation requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out
17 | Controls & DCIM | §C.1.i | Meta FacNet and Data Center Infrastructure Management (DCIM): Note: Dynamo is a real-time power monitoring and protection reliability system that protects Meta’s power distribution network from power overages, spikes, and unplanned power surges. | TFO | Comply (part); Deviation (part); Exception (part) | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to monitoring all specified electrical parameters to meet Dynamo and line of demarcation requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out
17 | Controls & DCIM | §C.2 | Meta FacNet and Data Center Infrastructure Management (DCIM): Each DCIM monitoring point and alert must be thoroughly tested and verified through the DCIM tooling with Ignition. | TFO | Comply (part); Deviation (part); Exception (part) | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Meta DCIM monitoring point and alerting testing and verification requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out
17 | Controls & DCIM | §C.3 | Meta FacNet and Data Center Infrastructure Management (DCIM): DCIM integration point naming must align with DCIM naming standards (BMS-PLAN-348 – FDM Playbook Rev 1.0). | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | DCIM integration point naming will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's BMS and EPMS point naming and numbering standards. Compliance with, deviation from, or exception to dual naming, re-naming, or aligning with Meta DCIM naming standards per BMS-PLAN-348 - FDM Playbook Rev 1.0 will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out
17 | Controls & DCIM | §C.3.i | Meta FacNet and Data Center Infrastructure Management (DCIM): If LL equipment naming differs from DCIM integration point naming, label containing DCIM point name is to be provided on equipment being integrated. | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | DCIM integration point naming will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's BMS and EPMS point naming and numbering standards. Compliance with, deviation from, or exception to providing equipment labeling with DCIM, BMS, or EPMS point name will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out
5 | §1 | N/A | Intent of Document | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Landlord will Comply, Deviate, or take Exception to any and all Meta Data Center requirements as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below.
6 | §3 | N/A | Related Documents: Owner's Project Requirements (OPR) | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Landlord will Comply, Deviate, or take Exception to any and all Owner's Project Requirements (OPR) requirements as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below.
6 | §4 | N/A | Design Criteria | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Landlord will Comply, Deviate, or take Exception to any and all Meta design criteria and basis of design as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below.
6 | Electrical | §B.a.i | Data Hall Server Row Power: 480/277V busways preferred (415/240V acceptable as alternative), lengths per rack layout. | TFO | Comply (part); Exception (part) | 480/277V power will not be provided. All server row power will be 415/240V. Row length and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work.
5 | §2 | Bullet #4 | Landlord Design Team Expectations: Landlord shall deliver record docs and models for future Meta reference. | Base Build (part); TFO (part) | Comply | Record documents and models shall be in electronic form (REVIT, CAD, or PDF) and shall be in file formats mutually agreed upon by Landlord and Tenant.
5 | §2 | Bullet #5 | Landlord Design Team Expectations: The project must adhere to all required building codes to meet local agency approval. | Base Build (part); TFO (part) | Comply | No comment.
7 | Electrical | §B.a.iii | Data Hall Server Row Power: Row busway to be rated 800A and fed from 100% rated 800A breaker (2x400A configuration acceptable as well). Busway size to be reviewed/finalized during tenant fit out design development. | Base Build | Comply | Power Distribution Unit (PDU) output breakers which feed the row busways are currently 600AF/AT. All PDU output breakers will be changed to 800AF/AT, 3P, 100% rated breakers as part of Base Building scope of work.
7 | Electrical | §B.b.i | Reserve Connections: LL to provide a Reserve/catcher system. Each row has a manual transition to reserve; these connections may be daisy-chained such that one reserve switchboard is sufficient for all rows within a data hall. For all equipment serving more than one fault domain, the transition to reserve must be automatic. Intent is to be fully concurrently-maintable for all equipment serving more than one row, and fault tolerant for all equipment serving more than one failure domain. | Base Build (part); TFO (part) | Deviation | Each PDU will have a reserve catcher system with automatic transfer switches (ATS's) as part of the Base Build. PDUs are concurrently maintanable. Manual transfer switches (MTS's) for each row can be provided as part of Tenant Fit-Out (TFO) scope-of-work.
7 | Electrical | §B.a.v | Data Hall Server Row Power: Each row to have manual transition between primary and reserve power sources | TFO | Comply | Each row will have manual transition between primary and reserve power sources located in the white space. Manual transfer switches (MTS's) will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
7 | Electrical | §B.a.vi | Data Hall Server Row Power: Accessibility/maintenance: Busway horizontal access requirement is <2’ from front of the rack to the busway itself (not front of tap box). | TFO | Comply | Power busway locations will be determined as part of Tenant Fit-Out (TFO) scope of work.
7 | Electrical | §B.a.vii | Data Hall Server Row Power: Each electrical distribution block shall never feed more than 2 data hall suites | Base Build | Comply | No comment.
7 | Electrical | §B.c.i | UPS-Backed Ancillary Power: Provide dual 120V, 20A/1P, UPS backed circuits from diverse panels to meter enclosures. | TFO | Comply | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning.
7 | Electrical | §B.c.iii | UPS-Backed Ancillary Power: Provide dual UPS-backed power to all IDF racks | Base Build | Comply | No comment.
7 | Electrical | §B.d.i | Convenience Power: Cord reels (GFCI) or convenience receptacles are required to be accessible at every row. | TFO | Comply | Cord reels (GFCI) or convenience receptacles will be accessible at every row and will be provided as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §C.a.i | Network System Row Power: (2) 415/240V dual UPS-backed busways in network suite. All remaining network busways to be single-corded, non-UPS-backed, 480/277V preferred (415/240V acceptable as alternative). Quantity of UPS backed rows to be reviewed/finalized during tenant fit out design development. | TFO | Comply (part); Deviation (part); Exception (part) | 480/277V power will not be provided. All network row power will be 415/240V and will be UPS backed. Quantity of rows, row length, and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work.
7 | Electrical | §B.f.i | Transfer Inhibit: Landlord-provided transfer inhibits for each block redundant system to ensure the reserve system is not overloaded. Include capability to prevent automatic transfer in case a bypass procedure is being performed downstream. | Base Build | Comply | No comment.
7 | Electrical | §B.g.i | Power System Study: For row level breakers, please ensure the minimum settings are such: 1. LTPU: Busway full load rating (example: 400A) 2. LTD: 12, I2T on (ensure within cable / busway thermal limits) 3. STPU: 2x LTPU 4. STD: 0.2, I2T off 5. Inst: 10x LTPU | TFO | Comply | Row level breaker settings will be programmed as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §B.g.ii | Power System Study: Ensure breakers upstream of row level coordinate with the settings above | TFO | Comply | Row level breakers will be fully coordinated with all upstream breakers as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §C.a.ii | Network System Row Power: Lengths per rack layout. | TFO | Comply | Quantity of rows, row length, and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §C.a.iii | Network System Row Power: Each busway to be rated 800A and powered from 800A, 100% rated breakers (2x 400A configuration acceptable as well). Busway size to be reviewed/finalized during tenant fit out design development. | Base Build | Comply | Power Distribution Unit (PDU) output breakers which feed the row busways are currently 600AF/AT. All PDU output breakers will be changed to 800AF/AT, 3P, 100% rated breakers as part of Base Building scope of work.
8 | Electrical | §C.a.v | Network System Row Power: Accessibility/maintenance: Busway horizontal access requirement is <2’ from front of the rack to the busway itself (not front of tap box). Any larger distance requires further evaluation and alignment with Meta. | TFO | Comply | Power busway locations will be determined as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §D.a | Admin and DC Support Spaces: Refer to DSS for power and grounding requirements. | TFO | Comply | Any and all power and grounding for admin and data center support spaces will be provided as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §E.a | Lighting: Lighting to be LED; match landlord fixture types | Base Build (part); TFO (part) | Comply | Landlord is providing a baseline lighting design for the data halls as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §E.b | Lighting: Light levels to meet Meta standards in accordance with the DCC. | Base Build (part); TFO (part) | Comply | Landlord is providing a baseline lighting design for the data halls as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §F.a | Nameplates: All Meta equipment to have a nameplate that is legible from ground level | TFO | Comply | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements.
9 | Mechanical | §A.1 | Admin Offices and Support Spaces: Office/Support space cooling design to match Meta temperature and humidity standards as listed in the Data Center Space Standards (DCSS) document. | TFO | Comply (part); Deviation (part); Exception (part) | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to office space and support space cooling design requirements per Meta "Data Center Space Standards (DCSS)" document requirements will be determined as part of Tenant Fit-Out (TFO) scope of work.
8 | Electrical | §F.b | Nameplates: Nameplate to include at least the following information: i. Equipment Name ii. Fed from: iii. Source 1 and source 2 information (if applicable) | TFO | Comply | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements.
8 | Electrical | §F.c | Nameplates: Examples shown below: | TFO | Comply | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements.
9 | Mechanical | §A.2 | Admin Offices and Support Spaces: Size supplementary cooling/heating systems, if landlord’s air handler capacity is unable to meet office/support requirements, at design ambient ASHRAE conditions (0.4%cooling, 99.6% heating) | TFO | Comply | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work.
9 | Mechanical | §A.3 | Admin Offices and Support Spaces: Supplementary ventilation to be based on ASHRAE 62.1 | TFO | Comply | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work.
9 | Mechanical | §A.4 | Admin Offices and Support Spaces: Minimum admin space humidity of 30% RH | TFO | Comply | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work.
9 | Mechanical | §B.1 | Studies and tooling: Development of rack loading based on site electrical distribution and review of landlord CFD (computational fluid dynamic) model to support Meta rack layout and temperature/humidity SLA requirements for all critical spaces. | TFO | Comply | Development of rack loading, rack location determination, and review of Landlord data hall CFD model(s) will be provided as part of Tenant Fit-Out (TFO) scope of work.
10 | Mechanical | §D.1.i | Rack-level waterside requirements: Maximum 86°F [30°C] supply water temperature. Typical operating temperatures of 80°F [27°C]. | Base Build (part); TFO (part) | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
10 | Mechanical | §D.1.ii | Rack-level waterside requirements: 18°F ΔT [10°C ΔT] waterside rack ΔT. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
10 | Mechanical | §D.1.iii | Rack-level waterside requirements: Minimum 0.4 GPM / kW [1.5 LPM / kW] water flow rate. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
10 | Mechanical | §D.1.iv | Rack-level waterside requirements: 40 PSI ΔP [241-276 kPa ΔP] pressure drop across the rack. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
10 | Mechanical | §D.1.v | Rack-level waterside requirements: The technical water loop header needs to be sized to align with electrical distribution capacity for that row. I.e. The technical water loop needs to be sized to assume 100% of the server capacity in the row is water cooled. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
10 | Mechanical | §D.1.vi | Rack-level waterside requirements: 1-¼” drops at each rack position. Elevations and positions of drops to align with layouts drawings (provided as part of BoD Documents) | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work.
10 | Mechanical | §D.1.vii | Rack-level waterside requirements: Quick connects to be BSPP thread. Approved vendors: Parker, CEJN, Safeway | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work.
10 | Mechanical | §D.1.viii | Rack-level waterside requirements: Additional 3” drops at rack positions as shown in the diagram below for rows of up to 30 servers. For rows greater than 30 servers need to agree 3” drop locations with Meta on a case by case basis. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work.
10 | Mechanical | §D.1.ix | Rack-level waterside requirements: PG25 for the TW loop to be Dowfrost LC25. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work.
10 | Mechanical | §D.1.x.a | Rack-level waterside requirements, Cleanliness: Fill flush and treatment of TW loop shall meet Dow requirements for Dow LC25. Sample of water from the TW loop once construction is complete shall be sent to Dow for approval. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
10 | Mechanical | §D.1.x.b | Rack-level waterside requirements, Cleanliness: Landlord must guarantee that no solids greater than 25 micron in size shall pass through any of the liquid cooled servers. | TFO | Comply | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease.
11 | Mechanical | §D.2.i | Rack-level airside requirements: 65°F-85°F [18.3°C-29.4°C] supply air temperature. | Base Build | Comply | Airside SLAs will be as stated in Exhibit H of the Lease.
11 | Mechanical | §D.2.ii | Rack-level airside requirements: 20%-80% supply air relative humidity, non-condensing. | Base Build | Comply | Airside SLAs will be as stated in Exhibit H of the Lease.
11 | Mechanical | §D.2.v | Rack-level airside requirements: MERV 8 Recirculation Filters, MERV 13 OSA Filters | Base Build | Comply | Airside SLAs will be as stated in Exhibit H of the Lease.
11 | Mechanical | §D.3.i | Cooling distribution units (CDUs): Concurrently maintainable, feeding into a looped or manifold piping arrangement (or equivalent). | Base Build | Comply | Waterside SLAs will be as stated in Exhibit H of the Lease.
11 | Mechanical | §D.4 | Liquid cooling infrastructure inside data halls and network rooms to independently support cooling failure domain, so that cooling failure does not impact more than one failure domain unless otherwise agreed with Meta. Landlords shall provide Meta alternative liquid cooling fault domain schemes with cost and schedule impacts for review. | Base Build | Comply | Each data hall has a dedicated cooling infrastructure such that any data hall level cooling failure does not affect any other data hall.
11 | Architectural | §A.1.i.a | Programming & Circulation, Admin Office space: The first building on the campus will be the main building and need desk space for 35 employees. | TFO | Comply | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work.
11 | Architectural | §A.1.i.c | Programming & Circulation, Admin Office space: See “Open Office” in Meta Data Center Space Standards for configuration requirements. | TFO | Comply (part); Deviation (part); Exception (part) | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Office/Storage Space configurations requirements per the "Open Office" section(s) of the Meta "Data Center Space Standards (DCSS)" document requirements will be determined as part of Tenant Fit-Out (TFO) scope of work.
11 | Architectural | §A.1.i.b | Programming & Circulation, Admin Office space: All subsequent buildings on the campus will require desk space for 20 employees. | TFO | Comply | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work.
12 | Architectural | §A.2.iv.b | Programming & Circulation, Corridors and Pathway, Freight Elevators: Minimum of two per building; three is preferred | Base Build | Comply | The building has two (2) freight elevators.
12 | Architectural | §A.2.iv.d | Programming & Circulation, Corridors and Pathway, Freight Elevators: 9’ Minimum door height and 7’-3” opening width | Base Build | Comply | No comment.
13 | Architectural | §B.1 | Audio Visual: Office Spaces should follow Meta’s current AV Standard Designs. See Meta Data Center Space Standards. Refer to Standards Hub for information on lease programming in section 3a. | TFO | Comply | Audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work.
13 | Architectural | §B.1.i | Audio Visual: One Training room allowed per campus, no Multipurpose rooms are scoped for Meta lease campuses. | TFO | Comply | Training room(s), multiple purpose room(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting.
13 | Architectural | §B.1.ii | Audio Visual: One Meet Up space with either a single monitor @ 86” or three monitors @ 55” allowed per campus. In the event of multiple Meet up spaces within campus, The AV setup will only support procurement for one AV set up per campus. | TFO | Comply | Meet Up space(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting.
13 | Architectural | §B.1.iii.a | Audio Visual: Two wall-mounted monitors per set @ 55” in the Shipping & Receiving office (none in Loading Dock area) for AV dashboards | TFO | Comply | Shipping & Receiving office(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting.
13 | Architectural | §B.1.iii.b | Audio Visual: EE service desk/helpdesk, IT vending machine, IT smart lockers, IT storage spaces | TFO | Comply | EE service desk(s)/helpdesk(s), IT vending machine(s), IT smart lockers, IT storage spaces and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting.
14 | Architectural | §E.3.iii.a | Building Opening & Hardware, Doors, Door Hardware: Lock and latch sets, including electrified, to be heavy duty commercial mortise type | Base Build | Comply | No comment.
14 | Architectural | §E.3.iii.b | Building Opening & Hardware, Doors, Door Hardware: Use electric strikes only on aluminum/glass entrance doors as a last resort | Base Build | Comply | No comment.
14 | Architectural | §E.3.iii.c | Building Opening & Hardware, Doors, Door Hardware: Provide key override at each electric strike and electrified lock set | Base Build | Comply | No comment.
14 | Architectural | §E.3.iii.d | Building Opening & Hardware, Doors, Door Hardware: Use push pad style exit devices where required to satisfy code or local jurisdiction requirements | Base Build | Comply | No comment.
14 | Architectural | §E.3.iii.f | Building Opening & Hardware, Doors, Door Hardware: Lever sets: heavy-duty mortise hardware | Base Build | Comply | No comment.
15 | Architectural | §E.3.iii.g | Building Opening & Hardware, Doors, Door Hardware: Hinges: stainless steel heavy duty mortised butt-hinges in accordance with manufacturer’s recommendations at swing doors | Base Build | Comply | No comment.
15 | Architectural | §E.3.iii.h | Building Opening & Hardware, Doors, Door Hardware: Hinges to be tamper-resistant (NRP) throughout | Base Build | Comply | No comment.
15 | Architectural | §E.3.iii.i | Building Opening & Hardware, Doors, Door Hardware: Flush bolts/coordinators on all pairs with an inactive leaf | Base Build | Comply | No comment.
15 | Architectural | §E.3.iii.j | Building Opening & Hardware, Doors, Door Hardware: Closers: heavy duty hydraulic | Base Build | Comply | No comment.
15 | Architectural | §E.3.iii.k | Building Opening & Hardware, Doors, Door Hardware: Provide seals for weather tightness and sound dampening | Base Build | Comply | No comment.
15 | Architectural | §E.3.iii.n | Building Opening & Hardware, Doors, Door Hardware: EOR responsibility to ensure all hardware is fully compatible with the door manufacturer and meets all building codes | Base Build | Comply | No comment.
16 | Architectural | §G.3 | Interior Construction & Materials: Hot Aisle Containment shall allow for racks up to 8’-0” in height. Ensure airflow is blocked in the gap between racks and bottom of containment while allowing containment to move up and down slightly. Infill panels shall be provided for 10% of rack positions. | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | Architectural | §G.4 | Interior Construction & Materials: Review flatness & weight capacity criteria for robotics & servers with Meta | Base Build | Comply | Flatness and floor loading capacity will be as detailed and shown in the Landlord's structural drawings, plans, specifications, and basis of design.
16 | Architectural | §G.5 | Interior Construction & Materials: Ceilings - No Meta-specific loading criteria. Design and construct in accordance with applicable local building codes, regulations, and industry standards. | Base Build | Comply
16 | Architectural | §H.1 | Furniture: All Furniture in Meta spaces is OFOI. AV scope must be closely coordinated with the Meta Furniture team for conference room integration. | TFO | Comply | All furniture and AV items will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §I.1 | Rack Height Accommodation and Airflow: Hot Aisle Containment shall allow for racks up to 8'-0" in height. | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §I.2 | Rack Height Accommodation and Airflow: Ensure airflow is blocked in the gap between racks and the bottom of containment while allowing containment to move up and down slightly. | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §I.3 | Rack Height Accommodation and Airflow: Where IT equipment is not installed, or is not of a consistent height, an adjustable blanking panel(s) shall be provided to achieve a positive seal to mitigate air loss from the HAC. | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §I.3.i | Rack Height Accommodation and Airflow: Sliding HAC panels shall be provided to access the cable pathways | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §J.1 | Aisle Layout and Clearance: Hot aisles: 6 feet with 5 feet clear | TFO | Comply | Hot aisle width and clearances will be determined as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §J.2 | Aisle Layout and Clearance: Cold aisles: 14 feet with 7 feet clear | TFO | Comply | Cold aisle width and clearances will be determined as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §J.3 | Aisle Layout and Clearance: Ensure adequate clearance between HAC columns and adjacent racks to allow for easy maintenance and access | TFO | Comply | Precise clearances between HAC columns and adjacent racks will be determined as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §K.1 | HAC System Design and Interface: Connection, panel, and construction details of the containment interface should be designed to accommodate various rack heights within a row | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
16 | HAC Design | §K.2 | HAC System Design and Interface: The TORC system should be designed to accommodate different rack heights within a row | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | HAC Design | §L.1 | Safety and Code Compliance: HAC systems should be designed to meet seismic design requirements to ensure stability and integrity during earthquakes | TFO | Comply | Hot aisle containment (HAC) system will be designed and constructed to meet local seismic criteria and will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | HAC Design | §L.2 | Safety and Code Compliance: HAC systems should be constructed using fire-resistant materials to minimize the risk of fire spread | TFO | Comply | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | HAC Design | §L.3 | Safety and Code Compliance: All necessary grounding between LV racks and equipment to be provided | TFO | Comply | Grounding for LV racks, equipment, and hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | HAC Design | §M.1 | Labeling and Identification: Installing Row Position Labels in Production Rows and Row-End Labels denoting each row per design on both ends above HAC doors | TFO | Comply | Row position labels, row end labels, and hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | Controls & DCIM | §A.1 | System Overview: The leased facility incorporates two distinct and independently managed networks: the Landlord's operational network and Meta's dedicated Facilities Network (FacNet) | TFO | Comply | Installation of Meta's dedicated Facilities Network (FacNet) will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | Controls & DCIM | §B.1 | Landlord Owned Equipment: The control and monitoring of landlord mechanical and electrical equipment and the corresponding Building Management System (BMS) / Electrical Power Monitoring System (EPMS) shall be owned, operated and maintained by the Landlord. This should be developed in the base build scope of work. | Base Build | Comply | No comment.
17 | Controls & DCIM | §B.2 | Landlord Owned Equipment: The landlord shall allow for Web access (READ – ONLY) to Meta users to access both the landlords BMS and EPMS. | Base Build | Comply | Access to Landlord's BMS and EPMS will be provided via web portal and via API(s).
17 | Controls & DCIM | §C.4.i | Electrical Monitoring - DCIM: Meta dedciated Power Quality Meters (PQM's) for Landlord owned MSB's. | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
17 | Controls & DCIM | §C.4.i.a | Electrical Monitoring - DCIM: Separate meter enclosure shall be furnished with a monitored tamper switch. | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.4.i.b | Electrical Monitoring - DCIM: PQM to be wired (Modbus RS485) to a Meta dedicated gateway panel located within Meta space. | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.4.i.c | Electrical Monitoring - DCIM: Gateway panel shall connect directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.4.ii | Electrical Monitoring - DCIM: Meta dedciated PQM for Landlord PDU (Power Distribution Unit) (or equivalent line of demarcation) with branch circuit monitoring for row level metering. | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.4.ii.a | Electrical Monitoring - DCIM: PDU's will follow the same physical and network security requirements as MSB PQM (e.g., separate enclosure and wired to gateway panel) unless meter brick is located within Meta secure space, in which case it can connect direct to Meta’s facility network (FacNet). | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.4.ii.b | Electrical Monitoring - DCIM: Modbus TCP/IP integration to Meta’s facility network (FacNet). | TFO | Comply | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.i | Mechanical Monitoring - DCIM: Data Hall | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.i.a | Mechanical Monitoring - DCIM: Temperature and Humidity monitoring for every cold aisle. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.i.a.1 | Mechanical Monitoring - DCIM: Instruments to be provided with magnet backing and sufficient cable slack to allow placement at any rack position in the cold aisle. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.i.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the data hall. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.i.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.i.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.ii | Mechanical Monitoring - DCIM: Network Core Room/s | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.ii.a | Mechanical Monitoring - DCIM: Temperature and Humidity monitoring for every cold aisle. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.ii.a.1 | Mechanical Monitoring - DCIM: Instruments to be provided with magnet backing and sufficient cable slack to allow placement at any rack position in the cold aisle. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.ii.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the room. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.ii.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.ii.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii | Mechanical Monitoring - DCIM: Technical Water | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.a | Mechanical Monitoring - DCIM: The following is to be monitored: | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Supply Water Temperature | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Return Water Temperature | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Differential Pressure | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Flow Rate | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the data hall. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
18 | Controls & DCIM | §C.5.iii.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
19 | Controls & DCIM | §C.5.iii.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
19 | Controls & DCIM | §C.5.iv | Mechanical Monitoring - DCIM: Cooling Distribution Units (where applicable) | TFO | Comply | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work.
19 | Controls & DCIM | §C.6.i | Meta FacNet Security: Meta requires that all products, equipment, systems, components, and subcomponents comply with strict network compatibility and security requirements. Devices must be reviewed and approved by submitting Exhibit L, which includes detailed compliance forms such as the Product Compliance Form, Communications System Compliance Form, Component Compliance Form, and supporting documentation like communication diagrams and product data sheets. This submission ensures that devices meet Meta's network and security standards before approval for use. | TFO | Comply | Landlord will submit Exhibit L forms as required for Meta's review and approval. Submission of the Exhibit L forms and compliance with, deviation from, or exception to Meta's requirements will be determined as part of Tenant Fit-Out (TFO) scope of work.
19 | Security | §A.a | General: Physical security, including guard force, operational policies/procedures, access controls, badging, intrusion detection and video surveillance will be the primary responsibility of the Landlord, unless otherwise noted in the lease. | Base Build | Comply | No comment.
19 | Security | §A.b | General: All security requirements within this document, with the exception of those installed as part of the Meta fit out, are required at lease commencement. Any exceptions must be reviewed and approved by Meta. | Base Build | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to any Meta Security requirements for each Program Design Criteria (PDC) section, subsection, or line item is as stated below. Installation of equipment to support each PDC security requirement will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status.
19 | Security | §A.c | General: Security requirements that are part of the Meta Fit Out are required to be active before Meta Fit out completion. | TFO | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to any Meta Security requirements for each Program Design Criteria (PDC) section, subsection, or line item is as stated below. Installation of equipment to support each PDC security requirement will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status.
19 | Security | §B.a | Compliance: The landlord shall comply with the latest ISO/IEC 27001 Information Technology -Security Techniques - Information Security Management Systems - Requirements. | Base Build | Comply | No comment.
19 | Security | §B.b | Compliance: The Landlord shall comply and provide evidence of compliance and certification on an annual basis. | Base Build | Comply | No comment.
19 | Security | §B.c | Compliance: The Landlord shall comply and provide evidence of compliance with the SOC2 Standards on an annual basis. | Base Build | Comply | The initial evidence of compliance (SOC2 report) will be provided once the facility has been in operation for one (1) full calendar year (e.g., if the facility is completed in October 2026, the initial SOC2 report will be for 2027 and will be provided in 2028). Landlord can provide bridging letters as required by Tenant.
19 | Security | §C.a | Submittals: The Landlord shall provide project design drawings, specifications and commissioning reports to Meta for review and comment throughout the design and construction process to ensure compliance with the security requirements included in the Lease Agreement. | Base Build (part), TFO (part) | Comply | Submittals for security related items for the Base Build scope-of-work will be provided by Landlord. Submittals for security related items for the Tenant Fit-Out (TFO) scope-of-work will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Landlord reserves the right to reasonably redact submittal information to the degree that it does not impact Meta's ability to evaluate for compliance to requirements.
20 | Security | §C.a | Coordination & Inspections: Landlord shall communicate the following non-design & design related information to Meta Security prior to the design kick off date: i. Team member roles & responsibilities. ii. Paths of escalation. iii. Distribution Lists for drawing packages. iv. Security BoD (Basis of Design) or Building Security Narrative. v. List of Landlord approved security devices to be deployed (model/ part number, etc…) | Base Build (part), TFO (part) | Comply | Information for security related items for the Base Build scope-of-work will be provided by Landlord. Information for security related items for the Tenant Fit-Out (TFO) scope-of-work will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Landlord reserves the right to reasonably redact submittal information to the degree that it does not impact Meta's ability to evaluate for compliance to requirements.
20 | Security | §C.b | Coordination & Inspections: During design, Landlord shall ensure that all information communicated to Meta Security for general coordination (e.g., design drawings, specifications, security device selection & installation/commissioning, construction schedules, supporting infrastructure, space hand-over dates, etc.) are based on the most recent version of the design to facilitate efficient coordination between Security, Meta’s design teams, and the landlord’s security designer. | Base Build (part), TFO (part) | Comply | No comment.
20 | Security | §C.c | Coordination & Inspections: If Meta fitout security designer differs from base build security designers, ensure coordination between security design occurs. | Base Build (part), TFO (part) | Comply | No comment.
20 | Security | §C.d | Coordination & Inspections: During construction, regular fortnightly coordination meetings beginning at least two months ahead of planned security go live dates, to coordinate site and space access, space lockdown and other items. | Base Build (part), TFO (part) | Comply | No comment.
20 | Security | §C.e | Coordination & Inspections: Meta Security requests to conduct a minimum of two site observations during construction to ensure scope is being executed correctly in accordance with the contract documents. These will generally occur prior to base-build security completion and Meta fit out security completion. Prior to the observations occurring, Meta Security will communicate the dates & associated agendas for each walk at least 30 days prior to it occurring. | Base Build (part), TFO (part) | Comply | No comment.
20 | Security | §D.a | Environmental Design and Construction: Telecommunications Vaults | Base Build (part), TFO (part) | Comply (part); Deviation (part) | See comments to §D.a.i and §D.a.ii, below.
20 | Security | §D.a.i | Environmental Design and Construction: All telecommunication vaults, on data center property, shall be located within security perimeter fence line and physically secured by the landlord to prevent unauthorized access (e.g., lockable bolt, lockable cover, padlock) | Base Build (part), TFO (part) | Comply (part); Deviation (part) | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
20 | Security | §D.a.ii | Environmental Design and Construction: Subject to Meta review and approval, telecommunication vaults located outside the secure perimeter, shall be locked and alarmed to detect intrusion. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
20 | Security | §D.b | Environmental Design and Construction: Fence | Base Build | Comply | No comment.
20 | Security | §D.b.i | Environmental Design and Construction: A secure perimeter around the property shall be provided including a physical barrier to restrict access by pedestrians and vehicles (e.g., fence) and one or more secure entrances to provide vehicle and pedestrian access through the secure perimeter. | Base Build | Comply | No comment.
20 | Security | §D.b.ii | Environmental Design and Construction: The fence shall contain no person-passable openings, except those required for any secure entries, and reasonably restrict access by climbing by maintaining a minimum height above grade of 8 feet with an anti-climb topper. | Base Build | Comply | No comment.
21 | Security | §D.b.iii | Environmental Design and Construction: The fence shall contain no person-passable openings, except those required for any secure entries, and reasonably restrict access by climbing by maintaining a minimum height above grade of 8 feet with an anti-climb topper. | Base Build | Comply | No comment.
21 | Security | §D.c | Environmental Design and Construction: Site Entrance | Base Build | Comply | No comment.
21 | Security | §D.c.i | Environmental Design and Construction: Secure entries shall allow for verification of business need for all access by personnel, pedestrians or in vehicles prior to permitting access through the secure perimeter. | Base Build | Comply | No comment.
21 | Security | §D.c.i | Environmental Design and Construction: Secure entries shall utilize access control and video surveillance systems to document site access and provide a historic record for investigations. | Base Build | Comply | No comment.
21 | Security | §D.d | Environmental Design and Construction: Building Requirements | Base Build | Comply | No comment.
21 | Security | §D.d.i | Environmental Design and Construction: A continuous secure envelope around Meta’s Leased Space including walls, doors, and access points (including below raised floors and above drop ceilings) shall be provided. | Base Build | Comply | No comment.
21 | Security | §D.d.ii | Environmental Design and Construction: All Landlord equipment, support spaces, network infrastructure support spaces (e.g., MDF, BDF, etc.), and electrical infrastructure support space shall be physically separated from the Meta’s leased space. | Base Build | Comply | No comment.
21 | Security | §D.d.iii | Environmental Design and Construction: The Landlord shall provide secure cages within Meta space to separate General System Racks from Production Racks. Cage design shall be in accordance with Meta’s requirements. | TFO | Comply | Secure cages within Meta spaces, if required, will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
21 | Security | §D.d.iv | Environmental Design and Construction: Meta’s Production Network gear which performs fabric aggregation functions shall be located within the Network Suite or GS.MDF and be physically separated from the data hall. Meta to advise during design. | TFO | Comply | Any work required to physically separate Meta's production network gear from the data hall will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
21 | Security | §E.a | Secured Cage or Mesh Wall Requirements: General | Base Build (part), TFO (part) | Comply | See comments to §E.a.i, §E.a.ii, and §E.a.iii, below.
21 | Security | §E.a.i | Secured Cage or Mesh Wall Requirements: Secure cages/mesh walls are used to physically partition spaces within data centers to restrict physical access to a space (e.g. IDF, etc.) | Base Build (part), TFO (part) | Comply | Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
21 | Security | §E.a.ii | Secured Cage or Mesh Wall Requirements: When required, they shall not impede airflow or equipment operation. Impact on airflow and cooling shall be considered in the design. | Base Build (part), TFO (part) | Comply | No comment.
21 | Security | §E.a.iii | Secured Cage or Mesh Wall Requirements: Adhere to required clearances to adjacent equipment, exit paths, doorways, rack pathways, and other equipment. | Base Build (part), TFO (part) | Comply | Landlord will adhere to code-required clearances as part of the Base Build scope-of-work. Accommodation for specific clearances required by Meta will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
21 | Security | §E.b | Secured Cage or Mesh Wall Requirements: Design Requirements | Base Build (part), TFO (part) | Comply | See comments to §E.b.i, §E.b.ii, §E.b.iii, and §E.b.iv, below.
21 | Security | §E.b.i | Secured Cage or Mesh Wall Requirements: Secure cages shall be at least 8’ AFF or the height required for rack height, but not higher than tier 3 tray. | Base Build (part), TFO (part) | Comply | Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
21 | Security | §E.b.ii | Secured Cage or Mesh Wall Requirements: The cage shall be constructed from wire mesh panels attached to posts. | Base Build (part), TFO (part) | Comply | No comment.
21 | Security | §E.b.iii | Secured Cage or Mesh Wall Requirements: The maximum gap between the bottom of the mesh panel and the floor below shall be 2 inches. | Base Build (part), TFO (part) | Comply | No comment.
21 | Security | §E.b.iv | Secured Cage or Mesh Wall Requirements: If required, provide a screen or fabric attached to mesh for visual privacy. | TFO | Comply | Any privacy screens or panels required will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
21 | Security | §E.c | Secured Cage or Mesh Wall Requirements: Material | Base Build (part), TFO (part) | Comply (part); Deviation (part) | See comments to §E.c.i and §E.c.ii, below.
21 | Security | §E.c.i | Secured Cage or Mesh Wall Requirements: Wire Mesh: 1”x1” powder coated black wire mesh; 9-gauge (minimum) | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building cage or mesh wall wire mesh will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall wire mesh requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any wire mesh for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §E.c.ii | Secured Cage or Mesh Wall Requirements: Posts: 2”x2” post anchored to concrete slab or raised access floor (as applicable). If the cage is on a raised floor, then there is no need to extend below the raised floor. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building cage or mesh wall support posts will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall support post requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any support posts for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §E.d | Secured Cage or Mesh Wall Requirements: Doors | Base Build (part), TFO (part) | Comply (part); Deviation (part) | See comments to §E.d.i, §E.d.ii, and §E.d.iii, below.
22 | Security | §E.d.i | Secured Cage or Mesh Wall Requirements: All doors shall be wire-mesh doors with electrified hardware, door actuators, and applicable access control, and door position switch. Strobes and sounders may be installed at the behest of the landlord, Meta Security takes no exception to the installation of these devices. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building cage or mesh wall doors and access control will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door and access control requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any doors and access control for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §E.d.ii | Secured Cage or Mesh Wall Requirements: Secure cage door hinges shall be located on the interior (secure) side or utilize tamper- resistant hardware. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building cage or mesh wall door hinges and hardware will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door hinge and hardware requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §E.d.iii | Secured Cage or Mesh Wall Requirements: Secure cage doors shall be designed to prevent manipulation of interior (secure side) hardware from the exterior (unsecure side). A typical method is through incorporating anti-tamper steel sheeting to mitigate the risk of manipulation of door hardware from the non-secure side. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building cage or mesh wall door hardware and trim will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door hardware and trim requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any door hardware and trim for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §E.e | Secured Cage or Mesh Wall Requirements: Video Surveillance | Base Build (part), TFO (part) | Comply (part); Deviation (part) | See comments to §E.e.i and §E.e.iii, below.
22 | Security | §E.e.i | Secured Cage or Mesh Wall Requirements: Cameras shall provide ID level video coverage at both card readers as per video surveillance requirements section. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building video surveillance of cage or mesh wall ingress and egress locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta video surveillance requirements for cage or mesh wall ingress and egress locations can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any video surveillance of secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §E.e.ii | Secured Cage or Mesh Wall Requirements: Security cabling shall be contained within the caged area. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | Base Building security cabling for cage or mesh wall ingress and egress locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta security cabling requirements for cage or mesh wall ingress and egress locations can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any security cabling for cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §F.a | Loading dock: The loading dock shall be considered shared Meta space in which the Landlord will be responsible for providing, managing, and maintaining all aspects of the following security measures within the space, including as a minimum (i) Access Control System, (ii) Video Monitoring System. | Base Build | Comply | Base Building access control and video monitoring for the loading dock will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control or video monitoring systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §F.b | Loading dock: There shall be Landlord provided, managed, and maintained overview-level video coverage of the exterior of the loading dock. | Base Build | Comply | Base Building video monitoring for the loading dock will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video monitoring systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §F.c | Loading dock: Meta shall always have reasonable access to a loading dock and a freight elevator at all times (in common with other tenants of the Building), subject to the Building Rules and Regulations. | Base Build | Comply | No comment.
22 | Security | §F.d | Loading dock: Doors from the exterior into the loading dock shall be secured by the Landlord using 2-factor access control. | Base Build | Deviation | Base Building access control from the exterior into the loading dock is via card reader. Two-factor authentication (card-key plus biometric) can be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §G.a | Access Control: General | Base Build | Comply (part); Deviation (part); Exception (part) | See comments to §G.a.i through §G.a.vi, below.
22 | Security | §G.a.i | Access Control: The Landlord shall be responsible for providing, managing, and maintaining all aspects of the access control system for the entire Data Center, including within Meta leased space. This includes all cabling, pathways, rough-in, and devices for all access controlled doors. | Base Build | Comply | Base Building access control will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
22 | Security | §G.a.ii | Access Control: All exterior doors into the Data Center shall be access-controlled by the Landlord. | Base Build | Comply | No comment.
23 | Security | §G.a.iii | Access Control: The Landlord shall not traverse Meta leased space to access other Landlord space (electrical rooms, etc.) | Base Build | Comply | No comment.
23 | Security | §G.a.iv | Access Control: There shall be no designated path of egress from landlord/common space through Meta leased space, unless unavoidable and required by the AHJ and approved by the Meta. | Base Build | Comply | No comment.
23 | Security | §G.a.v | Access Control: There shall be no exterior doors that lead directly into Meta leased space unless unavoidable and required by the AHJ and approved by the Meta. | Base Build | Comply | No comment.
23 | Security | §G.a.vi | Access Control: Access control system shall adhere to OSDP version 2.2 or latest version | TFO | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to access control system requirements per OSDP version 2.2 or the latest version will be determined as part of Tenant Fit-Out (TFO) scope-of-work. Installation of access control system equipment to support each particular requirement of OSDP version 2.2 or the latest version will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status.
23 | Security | §G.b | Access Control: Meta Lease Space | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | See comments to §G.b.i through §G.a.ix, below.
23 | Security | §G.b.i | Access Control: Meta leased space shall be access-controlled using either a multi-factor authentication (2-fac) or single-factor authentication (1-fac) approach. | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.ii | Access Control: Multi-factor authentication requires two different types of identify factors to enter: (1) Something you have (e.g., Card, Key, etc.) AND EITHER (2) Something you know (e.g., PIN, Username/Password) or (3) Something you are ( e.g., Fingerprint, Facial Geometry, etc.). | Base Build (part), TFO (part) | Comply | Landlord standard multi-factor authentication is card-key plus biometric access control. Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.iii | Access Control: Single-factor identification is used for all access-controlled doors not implementing a multi-factor approach. | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.iv | Access Control: The type of access control provided for entry and exit of Meta leased space shall be dictated by the Meta's space type requirements (Refer to Device Matrix). | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v | Access Control: 2-factor authentication in and 1-factor authentication out shall be used in spaces that are designated as high-risk and/or critical to the success of the operation (Refer to Device Matrix). These spaces shall be designated by the Meta and include but not limited to: | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v.1 | Access Control: All spaces with access to or are part of the Metas’s network (e.g. MDF, Network Suite, Data Hall, IDF, etc.). | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v.2 | Access Control: High-value assets and/or equipment that will transmit or store user data is present (e.g. IBOS storage). | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v.3 | Access Control: The doorway is an entry to Meta’s leased space housing core datacenter infrastructure (e.g., Production Network spaces, Data Halls, etc.). | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v.4 | Access Control: General controls for the entire building’s facility operations systems are present. This includes but is not limited to spaces in which FacNet network switches or FacNet Client devices are present. | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v.5 | Access Control: All doors into ERAD spaces | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.v.6 | Access Control: Controls for the entire building’s security systems are present | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.vi | Access Control: If none of the above 2-factor conditions exist, a minimum of 1 factor of identity authentication shall be provided where one or more of the following conditions exist (Refer to Device Matrix): | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.vi.1 | Access Control: Controls for a portion of the security systems of the building are present | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
23 | Security | §G.b.vi.2 | Access Control: Physical security keys to the building are present. | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §G.b.vi.3 | Access Control: Mechanical equipment, electrical equipment, or other controls are present which could impact operations in a portion of the building | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §G.b.vi.4 | Access Control: Spaces which store equipment, spares, and other materials which are critical to data center operations | Base Build (part), TFO (part) | Comply | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §G.b.vii | Access Control: All access-controlled doors shall be actively monitored with an alerting mechanism that sends an alarm to on-site security personnel when unauthorized access is detected. This includes door forced open, door held open, etc. | Base Build (part), TFO (part) | Comply | Monitoring for data hall, POP room, electrical room, mechanical gallery, ancillary space, and other access controlled area doors will be provide as part of the Base Building scope-of-work. Monitoring for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cage) doors will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §G.b.viii | Access Control: All doors shall "fail secure" unless required for life safety egress. Doors that must "fail safe" for life safety egress shall have access control installed on the egress side that only acts to shunt the door alarm. | Base Build (part), TFO (part) | Comply | Landlord's standard is to have all doors "fail secure" except where required by local code or AHJ's for life safety egress. Data hall, POP room, electrical room, mechanical gallery, ancillary space, and other facility doors will be provide as part of the Base Building scope-of-work. Doors within Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §G.b.ix | Access Control: The access control system shall adhere to OSDP version 2.2 (or latest). Encryption (Secure Channel) shall be enabled and reader tamper alarm monitoring shall be employed. | TFO | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to access control system requirements per OSDP version 2.2 or the latest version will be determined as part of Tenant Fit-Out (TFO) scope-of-work. Installation of access control system equipment to support each particular requirement of OSDP version 2.2 or the latest version will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status.
24 | Security | §A.a | Video Surveillance: General | Base Build (part), TFO (part) | Comply | See comments to §A.a.i through §A.a.iii, below.
24 | Security | §A.a.ii | Video Surveillance: All building exterior entrances/doors shall have Landlord provided identification-level video surveillance coverage to monitor egress and ingress. | Base Build (part), TFO (part) | Comply | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §A.a.ii | Video Surveillance: All aspects of video surveillance within and outside Meta leased space shall be provided, managed, and maintained by the Landlord. | Base Build (part), TFO (part) | Comply | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §A.a.iii | Video Surveillance: Landlord shall provide identification level coverage (Pix/ft density of at least 50) of access-controlled doors from Landlord space into Meta space and vice versa. | Base Build (part), TFO (part) | Comply | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §A.b | Video Surveillance: Meta Leased Space/Fit-Out | TFO | Comply | See comments to §A.b.i through §A.a.vi, below.
24 | Security | §A.b.i | Video Surveillance: Meta leased space requires a layered video surveillance approach dependent on conditions within the space. This approach uses three classifications of coverage: (1) Overview level - (greater than 10 pix/ft density), (2) Recognition Level – (greater than 20 pix/ft density), (3) Identification Level – (greater than 50 pix/ft density) | TFO | Comply | No comment.
24 | Security | §A.b.ii | Video Surveillance: The location, number of cameras, and performance level of each camera within Meta leased space shall be dictated by the Meta's space type requirements. (Refer to Device Matrix) | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §A.b.iii | Video Surveillance: Overview level coverage shall be provided in spaces that hold high value assets or where work on high value assets is being done. (IBOS, Spoke, ERAD, etc.). These spaces shall have full coverage with no blackout or dead areas. | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §A.b.iv | Video Surveillance: Recognition level coverage (greater than 20 pix/ft density) shall be provided in the Data Hall. Cameras shall provide coverage throughout main aisles. | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
24 | Security | §A.b.v | Video Surveillance: ERAD spaces require specific coverage which includes: | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
25 | Security | §A.b.v.1 | Video Surveillance: Identification level coverage of all working stations with a minimum 1 frame per section (FPS) when no motion detected, and 10 FPS when motion is detected. | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
25 | Security | §A.b.v.2 | Video Surveillance: Cameras shall work with very low light (night vision mode) and shall have a sensitivity set to 5 percent motion detection. | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
25 | Security | §A.b.v.3 | Video Surveillance: Cameras in the ERAD room(s) should be set to continuously record. | TFO | Comply | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
25 | Security | §A.b.vi | Video Surveillance: Any Landlord IDF supporting the video management system for the Meta’s space shall be located outside of the Meta’s leased space. | TFO | Comply | No comment.
25 | Security | §B.a | Intrusion Detection and Resistance: Devices | Base Build | Comply (part); Deviation (part) | See comments to §B.a.i through §B.a.iv, below.
25 | Security | §B.a.i | Intrusion Detection and Resistance: All Meta dedicated spaces with glazed openings within 10ft. (3 m) of grade shall be laminated glass OR be provided with an anti-shatter film that is reviewed and approved by the Meta. | Base Build | Deviation | Base Building glazing will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Laminated glass or anti-shatter film will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
25 | Security | §B.a.ii | Intrusion Detection and Resistance: Intrusion detection capability shall be provided at all exterior doors (e.g. door held open and door forced open detection) to establish a secure building perimeter layer. | Base Build | Comply | No comment.
25 | Security | §B.a.iii | Intrusion Detection and Resistance: Intrusion detection capability shall be provided at all access controlled doors to detect and alert of unauthorized access. | Base Build | Comply | No comment.
25 | Security | §B.a.iv | Intrusion Detection and Resistance: The Landlord shall provide intrusion detection devices to monitor all man passable openings (e.g., louvers, hatches, etc.) into Meta leased space that are not physically secured to prevent unauthorized access (e.g., tamper-resistant fasteners, physical locks, etc.). | Base Build | Comply | No comment.
25 | Security | §B.b | Intrusion Detection and Resistance: Construction | Base Build (part), TFO (part) | Comply (part); Deviation (part) | See comments to §B.b.i and §B.b.ii, below.
25 | Security | §B.b.i | Intrusion Detection and Resistance: Where other tenants share a wall with Meta’s high-risk spaces, such walls shall extend below the raised access floor to the slab and to the ceiling by means of security grade wire mesh or other industry recognized secure barrier. Further such walls must be alarmed to detect intrusion. | Base Build | Comply | No applicable as Meta is the only tenant in the Building.
25 | Security | §B.b.ii | Intrusion Detection and Resistance: ERAD room design shall incorporate visual privacy features to prohibit visibility from outside of Meta Space | TFO | Comply | Visual privacy features for ERAD room(s) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
25 | Security | §C.a.i | Network Security: Network Access: Any device not owned and approved for use by Meta shall not be connected to any Meta network. (e.g., laptops, computers, cameras, BMS devices, EPMS devices, etc.) | TFO | Comply | No comment.
25 | Security | §C.b.i | Network Security: Network Interconnections: The Landlord’s, other tenant, or any other network shall not be connected to any Meta network. | TFO | Comply | No comment.
25 | Security | §C.c.i | Network Security: Network Interconnections: Network equipment, patch panels, interconnections, splice enclosures or telecommunication outlets, other than those owned or operated by Meta, shall not be collocated in a space or room containing those owned or operated by Meta. | Base Build (part), TFO (part) | Deviation | Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers.
26 | Security | §C.c.ii | Network Security: Network Interconnections: An exception to the above may be granted by the Meta for spaces where the Meta’s fiber infrastructure is intended to connect to carrier equipment. | Base Build (part), TFO (part) | Deviation | Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers.
26 | Security | §C.c.iii | Network Security: Network Interconnections: All video surveillance and access control devices shall be routed back to the Landlord’s IDF. There shall be no devices that connect to a Meta IDF, this includes devices that are located within the Meta’s leased space. | Base Build (part), TFO (part) | Comply | No comment.
26 | Security | §C.c.iv | Network Security: Network Interconnections: All cabling that supports video surveillance and access control shall be physically separated from Meta network cabling. This includes devices that are located within the Meta’s leased space. | Base Build (part), TFO (part) | Comply | No comment.
26 | Security | §C.d.i | Network Security: Telecommunication Pathways and Vaults between Meta-Lease Spaces: Exterior telecommunications pathways used to connect multiple Meta-leased spaces shall be secured and protected from unauthorized access. The Landlord shall be able to detect when those spaces are accessed. | Base Build (part), TFO (part) | Comply (part); Deviation (part) | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
26 | Security | §C.d.ii | Network Security: Telecommunication Pathways and Vaults between Meta-Lease Spaces: The Landlord shall notify Meta: (1) Before such a space is scheduled to be accessed so that Meta can monitor the network for intrusion, (2) Immediately when unscheduled access to such a space occurs. | Base Build | Comply | No comment.
26 | Security | §D.a | Device Matrix: High Risk Spaces Includes table listing (11) space types and their associated access control and video surveillance requirements. | Base Build (part), TFO (part) | Comply | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
27 | Security | §D.b | Device Matrix: Low/Medium Risk Spaces Includes table listing nine (9) space types and their associated access control and video surveillance requirements. | Base Build (part), TFO (part) | Comply | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
27 | Security | §D.Notes | Device Matrix: Notes: • Where there is an interconnecting door between the Network Hub and Megapod, Network Hub shall be 2-fac in, and 1-fac out into the Megapod • There shall be no designated path of egress from the Megapod through the Network Hub unless required by the AHJ and approved by Meta • Where a space requires 2-FAC and shares an interconnecting door with another Meta controlled space, it shall have 1-FAC access control in and out. • When a space requiring 2-fac shares an interconnecting door with another Meta space it shall have 1-factor access control installed on both sides. • Overview level - (greater than 10 pix/ft density), Recognition Level – (greater than 20 pix/ft density), Identification Level (ID) – (greater than 50 pix/ft density) | Base Build (part), TFO (part) | Comply | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
27 | Connectivity | §E.a | OSP Pathway: Carrier Pathways | Base Build | Comply | See comments to §E.a.i through §E.a.iv, below.
27 | Connectivity | §E.a.i | OSP Pathway: Pathways are to be provided to allow for outside carriers to enter facility from 4 diverse entry points | Base Build | Comply | No comment.
27 | Connectivity | §E.a.ii | OSP Pathway: Require minimum of 25’ separation between 4 diverse pathways | Base Build | Comply | No comment.
28 | Connectivity | §E.a.iii | OSP Pathway: Meta requires latitude/longitude to be provided for vault entry points to the campus duct ring. | Base Build | Comply | No comment.
28 | Connectivity | §E.a.iiv | OSP Pathway: Required to provide outside carriers with location to tie into the campus to provide service | Base Build | Comply | No comment.
28 | Connectivity | §E.b | OSP Pathway: Production Pathways | Base Build | Comply | See comments to §E.b.i through §E.b.ii, below.
28 | Connectivity | §E.b.i | OSP Pathway: Pathways are to be provided to interconnect the fiber cabling between buildings 1 through 3 for the back end (BE) and Front End (FE) network. | Base Build | Comply | There are only two (2) buildings on the campus. Production pathways will be provided to connect these buildings.
28 | Connectivity | §E.b.i.1 | OSP Pathway: BE Network | Base Build | Comply | See comments to §E.b.i.1.a, below.
28 | Connectivity | §E.b.i.1.a | OSP Pathway: There shall be a requirement of 2 diverse entry points with a required minimum of 25’ separation between the 2 diverse pathways. | Base Build | Comply | No comment.
28 | Connectivity | §E.b.i.2 | OSP Pathway: FE Network | Base Build | Comply | See comments to §E.b.i.2.a, below.
28 | Connectivity | §E.b.i.2.a | OSP Pathway: There shall be a requirement of 4 diverse entry points with a required minimum of 25’ separation between the 4 diverse pathways. | Base Build | Comply | No comment.
28 | Connectivity | §E.b.ii | OSP Pathway: Meta requires latitude/longitude to be provided for vault entry points to the campus duct ring. | Base Build | Comply | No comment.
28 | Connectivity | §F | ISP Pathways | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | See comments to §F.a. through §F.b.iii.4.b.iv, below.
28 | Connectivity | §F.a | ISP Pathways: ISP Pathways Supporting OSP | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | See comments to §F.a.i through §F.a.ii.5, below.
28 | Connectivity | §F.a.i | ISP Pathways: ISP Pathways Supporting OSP: Supporting Spaces | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | See comments to §F.a.i.1 through §F.a.i.2.c, below.
28 | Connectivity | §F.a.i.1 | ISP Pathways: Refer to the Building Interior and Structure section for space allocation and sizing requirements. | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to space allocation and sizing requirements will be as determined in the response to each requirement in the Building Interior and Structure section.
28 | Connectivity | §F.a.i.2 | ISP Pathways: Meet Me Room ("MMR") | TFO | Comply (part); Deviation (part) | See comments to §F.a.i.2.a through §F.a.i.2.c, below.
28 | Connectivity | §F.a.i.2.a | ISP Pathways: Each MMR requires 4 racks to be reserved for Meta use. These shall be (4) CPI 4-post racks. Refer to Power section for rack electrical requirements. | TFO | Comply | CPI 4-post racks for Meta use and associated electric power circuits will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
28 | Connectivity | §F.a.i.2.b | ISP Pathways: Landlord responsible for coordinating with Meta carriers and providing a provisioned MMR room in accordance with Meta carrier install schedules. | TFO | Deviation | Landlord will provide a provisioned MMR room as part of the Tenant Fit-Out (TFO) scope-of-work. Carrier install schedules will be as detailed with the Lease.
28 | Connectivity | §F.a.i.2.c | ISP Pathways: Pathways from MMR to Network Suites shall be designed by Meta. Installation of pathways shall be coordinated with Meta during design. | TFO | Comply | Pathways from MMR to Network Suites will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
28 | Connectivity | §F.a.ii | ISP Pathways: Entrance Facilities ("EF") | TFO | Comply (part); Deviation (part); Exception (part) | See comments to §F.a.ii.1.a through §F.a.ii.5, below.
28 | Connectivity | §F.a.ii.1 | ISP Pathways: All OSP conduits stubbing up into room to be coordinated with Meta. | Base Build | Exception | OSP conduit stub-up locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design.
28 | Connectivity | §F.a.ii.2 | ISP Pathways: Room walls shall be covered with fire-rated plywood. | Base Build | Comply | No comment.
28 | Connectivity | §F.a.ii.3 | ISP Pathways: Rooms are to be dedicated to Meta use. | Base Build | Deviation | Building entrance rooms (EF, POE, and POP rooms) may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers.
28 | Connectivity | §F.a.ii.4 | ISP Pathways: All ladder racks and trays in the room shall be designed and installed by Meta. | Base Build (part), TFO (part) | Deviation | Building entrance rooms (EF, POE, and POP rooms) will have ladder rack and/or fiber tray designed and installed by Landlord as part of the Base Build scope-of-work. Redesign and moves-adds-changes for ladder racks and/or fiber trays can be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
28 | Connectivity | §F.a.ii.5 | ISP Pathways: If the DC is a multistorey facility, the EF room shall also be utilized as a riser for OSP and ISP fiber. LL to provide all associated knockouts and pathways. | Base Build (part), TFO (part) | Comply | The building is a two (2) storey facility. Utilization of the building entrance rooms (EF, POE, and POP rooms) as a riser and engineering, furnishing, and installing pathways (and associated knockouts, core drilling, and other penetrations) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
29 | Connectivity | §F.b | ISP Pathways: ISP Pathways | TFO | Comply (part); Deviation (part); Exception (part) | See comments to §F.b.i through §F.b.iii.4.b.iv, below.
29 | Connectivity | §F.b.i | ISP Pathways: Cabling to support Front End (FE), Back End (BE), and General Systems (GS) shall be supported by ladder tray (Tier-1), Cable Trough (Tier-2), and basket tray (Tier-3, Tier-4, Tier-5, and Tier-GS). These tray tiers shall be implemented as needed to support the connectivity to/between meta network spaces (Network Suites, Megapods, GSIDF, etc.) and landlord spaces (POE and MMRs). | TFO | Comply | Ladder tray, cable trough, and basket tray to support Front End (FE), Back End (BE), and General Systems (GS) cabling will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
29 | Connectivity | §F.b.ii | ISP Pathways: Key Spaces | TFO | Comply (part); Deviation (part); Exception (part) | See comments to §F.b.ii.1 through §F.b.ii.4.b, below.
29 | Connectivity | §F.b.ii.1 | ISP Pathways: Refer to the Power section for power rating requirements per space. | TFO | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to space power rating requirements will be as determined in the response to each requirement in the Power section.
29 | Connectivity | §F.b.ii.2 | ISP Pathways: Network Suites | TFO | Exception | See comments to §F.b.ii.2.a, below.
29 | Connectivity | §F.b.ii.2.a | ISP Pathways: Provide four (4) Network Suites per Region. Network Suites must be able to be connected to each Megapod in the region while maintaining the 25% failure domain requirement. | TFO | Exception | Exception is taken to this item as it refers to Meta "Regions" and does not contain any scope-of-work requirements. The number of Network Suites to be provided will be as stated within the Lease.
29 | Connectivity | §F.b.ii.3 | ISP Pathways: Megapods | TFO | Exception | See comments to §F.b.ii.3.a and §F.b.ii.3.b, below.
29 | Connectivity | §F.b.ii.3.a | ISP Pathways: Each Megapod will contain a Main Distribution Frame (MDF) and dedicated IT rows. The MDF is a network space that provides connectivity between Megapods and Network Suites. | TFO | Exception | Exception is taken to this item as does not contain any scope-of-work requirements. The number of Megapods, Main Distribution Frames, and dedicated IT rows to be provided will be as stated within the Lease.
29 | Connectivity | §F.b.ii.3.b | ISP Pathways: Provide a maximum of forty-eight (48) Megapods per Region. | TFO | Exception | Exception is taken to this item as it refers to Meta "Regions" and does not contain any scope-of-work requirements. The number of Megapods to be provided will be as stated within the Lease.
29 | Connectivity | §F.b.ii.4 | ISP Pathways: Support spaces | TFO | Comply (part); Deviation (part); Exception (part) | See comments to §F.b.ii.4.a and §F.b.ii.4.b, below.
29 | Connectivity | §F.b.ii.4.a | ISP Pathways: Refer to the Building Interior and Structure section for space quantity and sizing requirements. | TFO | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to space quantity and sizing requirements will be as determined in the response to each requirement in the Building Interior and Structure section.
29 | Connectivity | §F.b.ii.4.b | ISP Pathways: Refer to the Power section for power rating requirements per space. | TFO | Comply (part); Deviation (part); Exception (part) | Compliance with, deviation from, or exception to space power rating requirements will be as determined in the response to each requirement in the Power section.
29 | Connectivity | §F.b.iii | ISP Pathways: GS Spaces | TFO | Comply | See comments to §F.b.iii.1 through §F.b.iii.4.b.iv, below.
29 | Connectivity | §F.b.iii.1 | ISP Pathways: GSIDF | TFO | Comply | See comments to §F.b.iii.1.a through §F.b.iii.1.b.ii, below.
29 | Connectivity | §F.b.iii.1.a | ISP Pathways: Meta uses the standard of determining GSIDF coverage using a diamond centered at the center of the IDF with a diagonal from the center of the diamond to a corner of the diamond with 235’ in length. Anything within the diamond is considered covered by the GSIDF. GSIDFs coverage must contain all Network Suites, Megapods, and common spaces completely. If coverage exceptions are needed, these will require Meta approval. | TFO | Comply | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
29 | Connectivity | §F.b.iii.1.b | ISP Pathways: Number of rack positions - 2 | TFO | Comply | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
29 | Connectivity | §F.b.iii.1.b.i | ISP Pathways: Rack 01 passive and Rack 02 active. | TFO | Comply | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
29 | Connectivity | §F.b.iii.1.b.i | ISP Pathways: iCPI 4-post for all racks | TFO | Comply | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
29 | Connectivity | §F.b.iii.2 | ISP Pathways: ADMIDF | TFO | Comply | See comments to §F.b.iii.2.a through §F.b.iii.2.b.ii, below.
29 | Connectivity | §F.b.iii.2.a | ISP Pathways: ADMIDF coverage is determined in a similar manner as GSIDFs utilizing the diamond coverage method. ADMIDF coverage must include all admin/office space for the floor the IDF is on. ADMIDF coverage is limited to the floor on which the ADMIDF is on. If coverage exceptions are needed, these will require Meta approval. | TFO | Comply | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.2.b | ISP Pathways: Number of rack positions – 4 | TFO | Comply | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.2.b.i | ISP Pathways: 2 active (Rack positions 02, 03) and 2 passive (Rack positions 01, 04). | TFO | Comply | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.2.b.ii | ISP Pathways: CPI 4-post for all racks | TFO | Comply | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.3 | ISP Pathways: GSMDF | TFO | Comply | See comments to §F.b.iii.3.a through §F.b.iii.3.b.ii, below.
30 | Connectivity | §F.b.iii.3.a | ISP Pathways: Co-located in each Network Suite, Rows 01 and 02. | TFO | Comply | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.3.b | ISP Pathways: Number of rows in each space - 2 | TFO | Comply | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.3.b.i | ISP Pathways: Number of rack positions in each row – 23 (Racks 01-03; 21-23 passive; Racks 04-20 active). | TFO | Comply | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.3.b.ii | ISP Pathways: CPI 4-post for Active Racks and CPI 2-post for Passive Racks. | TFO | Comply | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.4 | ISP Pathways: Riser Rooms | TFO | Comply | See comments to §F.b.iii.4.a through §F.b.iii.3.b.iv, below.
30 | Connectivity | §F.b.iii.4.a | ISP Pathways: For carrier and inter-building front-end connectivity, if multi-story building four risers are required to connect MDF spaces across floors. This is achieved by utilizing 4” conduit sleeves. Meta to coordinate the quantity of knockouts required. | TFO | Comply | The building is a two (2) storey facility. Engineering, furnishing, and installing risers, riser pathways, and associated conduit sleeves, knockouts, core drilling, and other penetrations will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.4.b | ISP Pathways: For intra-building back-end network connectivity, risers shall be placed between back-end MDF pairs. | TFO | Comply | The building is a two (2) storey facility. Engineering, furnishing, and installing risers, riser pathways, and associated conduit sleeves, knockouts, core drilling, and other penetrations will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.4.b.i | ISP Pathways: Riser configuration and slot dimension to be coordinated with Meta. | TFO | Comply | Riser configuration, penetration sizing & dimensions, and coordination with Meta will be determined and provided as part of the Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.4.b.ii | ISP Pathways: Preferred dimension 20”x 6” with 6 FT minimum between slots | TFO | Comply | Riser configuration, penetration sizing & dimensions, and distance between penetrations will be determined as part of the Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.4.b.iii | ISP Pathways: If perforations are located within accessible spaces, these must be secured in compliance with safety requirements. | TFO | Comply | Riser penetration locations, penetration accessability, and health & safety considerations will be addressed as part of the Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §F.b.iii.4.b.iv | ISP Pathways: Location and sizing of penetration zones for ISP pathways shall be coordinated with Meta for clash detection with other systems. | TFO | Comply | Riser configuration, penetration sizing & dimensions, and coordination with Meta will be determined and provided as part of the Tenant Fit-Out (TFO) scope-of-work.
30 | Connectivity | §G | Cabling | TFO | Exception | See comments to §G.a through §G.f.iii, below.
30 | Connectivity | §G.a | Cabling: All Cabling shall be designed and installed by Meta to meet the network requirements set by pINE and ENS. Cabling design is broken down by use case below and includes any outside plant (OSP), inside plant (ISP) and patch cabling. | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
30 | Connectivity | §G.b | Cabling: Carrier | TFO | Exception | See comments to §G.b.i through §G.b.iii, below.
30 | Connectivity | §G.b.i | Cabling: Outside Carrier to bring in new service via fiber optic cable to POE and/or MMR to provide lit and dark service for the Meta network | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
30 | Connectivity | §G.b.ii | Cabling: Services Handed off in the POE will tie to a house Meta Carrier cable which will be designed and routed by Meta on Tier-GS from POE to Network Suites. Cabling from a POE shall remain diverse from other POEs going to the same Network Suite. POE shall provide 4 diverse paths to each Network Suite. | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.b.iii | Cabling: Services Handed off in the MMR will tie to a house Meta Carrier cable which will be designed and routed by Meta on Tier-GS from MMR to Network Suites. Cabling from an MMR shall remain diverse from other MMRs going to the same Network Suite. MMRs shall provide a path to each Network Suite to be diverse from any other (minimum of 2 MMR for region) | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.c | Cabling: General Systems (GS) | TFO | Exception | See comments to §G.c.i through §G.c.v, below.
31 | Connectivity | §G.c.i | Cabling: 2 Network Suites will serve as the main GSMDFs for the region. GS will be a 2- path system for the region, where path 1 comes from one Network Suite and path 2 comes from the other | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.c.ii | Cabling: GS cabling shall be provided between Network Suites | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.c.iii | Cabling: All GSIDF and ADMINIDF shall be numbered in accordance with coordination with ENS | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.c.iv | Cabling: PTP Cabling shall connect to each Network suite providing 4 distinct paths for cabling | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.c.v | Cabling: MGMT and Console Fiber cabling shall be designed to support the production network (Front-End and Back-End) | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.d | Cabling: CorpNet | TFO | Exception | See comments to §G.d.i through §G.d.iii, below.
31 | Connectivity | §G.d.i | Cabling: All AP layouts shall be designed by Meta-RSE and installed by DEC managed vendors. | TFO | Exception | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.d.ii | Cabling: Overall floorplans, clearly indicating Meta-Exclusive Occupied space for AP layout and integration into Technology Drawing Sets. | TFO | Exception | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings.
31 | Connectivity | §G.d.ii.1 | Cabling: The “Overall AP Layout Plan” should show walls, doors, cable tray as full-tone and racks, HAC, shelving and room names as half-tone. | TFO | Exception | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings.
31 | Connectivity | §G.d.ii.2 | Cabling: Once the Overall Plans are provided to the RSE TDM they will send back AP Layouts to be included by the TEOR into the drawings set. | TFO | Exception | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings.
31 | Connectivity | §G.d.iii | Cabling: In addition the Overall AP Layout Plan will be AP mounting details for all AP mounting types occurring within the space. | TFO | Exception | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts or mounting details into Landlord's technology drawings.
31 | Connectivity | §G.e | Cabling: Front-End (FE) | TFO | Exception | See comments to §G.e.i through §G.e.iii, below.
31 | Connectivity | §G.e.i | Cabling: All Cabling required to connect layers in Network Suites, between Network Suites, and from Network Suites to Megapods | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.e.ii | Cabling: Designed as 4 diverse paths system between network topology layers | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.e.iii | Cabling: Leverages outside designated goalpost in Megapods | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.f | Cabling: Back-End (BE) | TFO | Exception | See comments to §G.f.i through §G.f.iii, below.
31 | Connectivity | §G.f.i | Cabling: All Cabling required to connect layers between Megapods by either direct cabling between megapods and/or cabling from Megapods to Network Suites | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.f.ii | Cabling: Designed as 2 diverse path system between network topology layers | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
31 | Connectivity | §G.f.iii | Cabling: Leverages inside designated goalpost in Megapods | TFO | Exception | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others.
32 | N/A | N/A | Interior lighting controls sequence of operations Table at top of page #32 | Base Build | Exception | Exception is taken to the "Interior Lighting Controls Sequence Of Operations" table at the top of page #32. Lighting controls and lighting controls sequence of operations (SOO) will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design.
32 | DAS/PTP | §A | Public Safety (ERRCS) DAS | Base Build | Deviation | See comments to §A.a through §A.a.iv, below.
32 | DAS/PTP | §A.a | Public Safety (ERRCS) DAS: Provide a Public Safety DAS system to comply with building and fire code requirements and to ensure first responder radio coverage is provided. | Base Build | Deviation | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work.
32 | DAS/PTP | §A.a.i | Public Safety (ERRCS) DAS: OEM: ADRF or Zinwave | Base Build | Deviation | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work.
32 | DAS/PTP | §A.a.ii | Public Safety (ERRCS) DAS: Active equipment to be UL2524 compliant | Base Build | Deviation | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work.
32 | DAS/PTP | §A.a.iii | Public Safety (ERRCS) DAS: Coordinate with local AHJ on required local frequencies/channels | Base Build | Deviation | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work.
32 | DAS/PTP | §A.a.iv | Public Safety (ERRCS) DAS: Coordinate rooftop antenna location to ensure donor signal functionality | Base Build | Deviation | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work.
32 | DAS/PTP | §B | Land Mobile Radio (LMR - Handheld radio) System | TFO | Deviation | See comments to §B.a through §B.c, below.
32 | DAS/PTP | §B.a | Land Mobile Radio (LMR - Handheld radio) System: Provide Meta personnel used handheld radio system | TFO | Deviation | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work.
32 | DAS/PTP | §B.b | Land Mobile Radio (LMR - Handheld radio) System: LMR system may share infrastructure with PS DAS with AHJ approval | TFO | Deviation | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work.
32 | DAS/PTP | §B.c | Land Mobile Radio (LMR - Handheld radio) System: OEM: Motorola | TFO | Deviation | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §C | Commercial (Cellular) DAS | Base Build (part), TFO (part) | Deviation | See comments to §C.a through §C.c, below.
33 | DAS/PTP | §C.a | Commercial (Cellular) DAS: Provide a cellular DAS solution to ensure in-building cell coverage is adequate and also meets e911 requirements. | Base Build (part), TFO (part) | Deviation | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §C.b | Commercial (Cellular) DAS: Landlord to obtain their own signal source from carriers (AT&T, Verizon, T-mobile) | Base Build (part), TFO (part) | Deviation | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §C.b.i | Commercial (Cellular) DAS: Recommend over-the-air as temporary and fiber base station installed as permanent | Base Build (part), TFO (part) | Deviation | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §C.b.ii | Commercial (Cellular) DAS: Provide a timing source (GPS) to support carrier base stations | Base Build (part), TFO (part) | Deviation | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §C.c | Commercial (Cellular) DAS: OEMs: Commscope, Solid, ADRF, Corning | Base Build (part), TFO (part) | Deviation | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | DLR agrees that we will wor kwith one of the selected DAS providers to have DAS installed post delivery of the datacenter suites at tennatns sole cost in the TFO
33 | DAS/PTP | §D | Precision-Timing-Protocol (GPS) | TFO | Comply | A Precision-Timing-Protocol (GPS) system will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §D.a | Precision-Timing-Protocol (GPS): Landlord to provide PTP pathway/infrastructure to accommodate 4 (four) PTP antennas | TFO | Comply | A Precision-Timing-Protocol (GPS) system with pathway/infrastructure to support four (4) PTP antennas will be provided as part of the Tenant Fit-Out (TFO) scope-of-work.
33 | DAS/PTP | §D.b | Precision-Timing-Protocol (GPS): Each PTP antenna is provided by Meta with a pre-terminated cable length attached. Coordinate length with Meta. The antenna OEN is Huber Suhner GPS over fiber. | TFO | Comply | No comment.
33 | DAS/PTP | §D.c | Precision-Timing-Protocol (GPS): Generally, the PTP antennas terminate to support each network suite (MDF), and coordinate final rack locations with Meta. | TFO | Comply | No comment.
33 | DAS/PTP | §D.d | Precision-Timing-Protocol (GPS): Landlord to provide two-inch or greater roof penetration with an independent pathway for each network suite | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.i | Precision-Timing-Protocol (GPS): A two-inch mast pipe to mount each antenna | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.ii | Precision-Timing-Protocol (GPS): Cable Containment from the antenna mast to the roof penetration | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.iii | Precision-Timing-Protocol (GPS): Continuous pathway from roof penetration to spaces dedicated for meta use | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.iv | Precision-Timing-Protocol (GPS): All cable pathways must maintain a bend radius of greater than 6 inches | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.v | Precision-Timing-Protocol (GPS): Antennas must be mounted below the nearest lightning arresting air terminal | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.vi | Precision-Timing-Protocol (GPS): At the minimum, a 180-degree view of the southern sky is required | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.vii | Precision-Timing-Protocol (GPS): No obstructions should be within a ten-degree angle from the horizon | TFO | Comply | No comment.
33 | DAS/PTP | §D.d.viii | Precision-Timing-Protocol (GPS): The antenna mast should be 6 feet away from metallic reflectors | TFO | Comply | No comment.
33 | DAS/PTP | §D.e | Precision-Timing-Protocol (GPS): Due to the class-4 lasers contained within the PTP system, Laser Warning signs should be incorporated into the design of PTP antenna locations | TFO | Comply | No comment.
|  |  |  | Comply | 240
|  |  |  | Part |  |  | 64
7
g

## Sheet1
Page # reference | Section | Subsection | Requirement | Scope | CDE | Status | Landlord comment | Meta Response | Paid By | Complexity | Jbrunen Response | CRitsema Responses | Responsible Party w/i DLR
5 | §1 | N/A | Intent of Document | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Closed | Landlord will Comply, Deviate, or take Exception to any and all Meta Data Center requirements as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below. |  | - | - | - | Header item only. | N/A
5 | §2 | Bullet #1 | Landlord Design Team Expectations: Landlord shall deliver mechanical, electrical, BMS/controls, plumbing, fire protection, architectural, structural, AV, and food services design and construction administration services for the fit-out of data halls, network suites, administration, and support spaces within colocation data center facilities. | Base Build (part); TFO (part) | Comply | Open | Design services and construction administration for certain aspects of mechanical, electrical, BMS/controls, plumbing, fire protection, architectural, and structural systems will be provided as part of Tenant Fit-Out (TFO) scope of work. All design services and construction administration for AV (audio visual) systems and food service will be provided as part of Tenant Fit-Out (TFO) scope of work. Food services design, build-out, and construction administration services will not be provided by Landlord. | Not accepted. We will need to have a microkitchen put in the admin space. | Meta | 2 | Digital Realty agrees to delivery of the kitchen requirement within the office premise area as part of the TFO process. | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
5 | §2 | Bullet #2 | Landlord Design Team Expectations: Landlord Design team is required to contract or coordinate with the following partners for scopes as indicated. | TFO | Comply | Open | Comply with coordinating directly with Meta for cabling; exception is taken to contracting or coordinating with RAS - Ronald Sadusky as food services design, build-out, and construction services will not be provided by Landlord; comply with contracting or coordinating with one of Meta's listed A/V consultants. | Not accepted. We will need to have a microkitchen put in the admin space. | Meta | 2 | Digital Realty agrees to delivery of the kitchen requirement within the office premise area as part of the TFO process. | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
5 | §2 | Bullet #3 | Landlord Design Team Expectations: The Landlord is required to provide documents for Meta reviews at 100%SD, 100%DD, 50%CD, and 95%CD. Review sessions shall be open for 5 business days to allow Meta team to comment. All comments shall be adjudicated by the Design Team and provided back to the Meta Team. The Deliverable Requirements Table for Meta fit-out scope is provided as a reference. | Base Build (part); TFO (part) | Comply (part); Exception (part) | Closed | Landlord will provide 95%CD or IFC (Issued for Construction) drawings for Base Build items for Tenant review. Exception is taken to providing 100%SD, 100%DD, and 50%CD drawings to Tenant as these milestones have already been completed prior to the Effective Date of the Lease. Landlord will provide 100%SD, 100%DD, 50%CD, and 95%CD drawings for Tenant Fit-Out (TFO) scope of work items as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Digital Realty | 1 | Accepted, no further comment | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
5 | §2 | Bullet #4 | Landlord Design Team Expectations: Landlord shall deliver record docs and models for future Meta reference. | Base Build (part); TFO (part) | Comply | Closed | Record documents and models shall be in electronic form (REVIT, CAD, or PDF) and shall be in file formats mutually agreed upon by Landlord and Tenant. |  | Digital Realty | 1 | Assumed to be accepted. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
5 | §2 | Bullet #5 | Landlord Design Team Expectations: The project must adhere to all required building codes to meet local agency approval. | Base Build (part); TFO (part) | Comply | Closed | No comment. |  | Digital Realty | 1 | Assumed to be accepted. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
6 | §3 | N/A | Related Documents: Owner's Project Requirements (OPR) | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) |  | Landlord will Comply, Deviate, or take Exception to any and all Owner's Project Requirements (OPR) requirements as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below. |  |  |  | - |  | Dan Kingman
6 | §3 | N/A | Related Documents: Data Center Space Standards | Base Build | Exception | Open | A general exception is take to Meta "Data Center Space Standards" requirements. Landlord is providing and Tenant is leasing data halls, office space, storage space, and ancillary space(s) based upon Landlord's building design and space planning requirements. | Not accepted. Meta has specific requirements for operating the tenant spaces, and need those to be fit-out per our standards. | Meta | 2 | Need to review DCSS document to understand requirement. |  | Dan Kingman
6 | §3 | N/A | Related Documents: Data Center Signage Guidelines | TFO | Comply | Open | Any and all signage required by Meta to conform to Meta "Data Center Signage Guidelines" requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Meta "Data Center Signage Guidelines" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Need alignment that Meta standards will be followed for Meta occupied spaces. | Meta | 1 | Need to review DCSG to understand requirement | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
6 | §3 | N/A | Related Documents: Meta PQM Performance Spec Rev 4 | TFO | Comply (part); Deviation (part); Exception (part) | Open | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. Compliance with, deviation from, or exception to "Meta PQM Performance Spec Rev 4" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | PQM coordination can be part of TFO but expectation is LL is complying with spec. | Meta | 3 | Need to review MetaPQM to understand requirement. | Need confirmation that we can fit dual CTs and PTs on equipment (one set for DLR metering, the second set for Meta metering). | Dan Kingman
6 | §4 | N/A | Design Criteria | Base Build (part); TFO (part) | Comply (part); Deviation (part); Exception (part) | Closed | Landlord will Comply, Deviate, or take Exception to any and all Meta design criteria and basis of design as they relate to each Program Design Criteria (PDC) section, subsection, or line item as stated below. | - | - | - | - | Header item only. | N/A
6 | Electrical | §A | Equipment metering a. Provide CT's, Branch Circuit Monitoring and Meter Enclosures as required per Meta PQM Performance Spec requirements (metering locations to be reviewed/finalized during tenant fit out design development). i. Metering locations to include: 1. Both Normal & Gen power, OR aggregate at all MSB's. 2. Metering of the common bus at all CDP/COD boards. 3. CDP/COD reserve loop feeder breaker in MSB Reserve board . 4. Row-level branch circuit monitoring. b. Provide all required interconnects between meter enclosures and LL equipment as well as Meta gateways (DCIM head end panels). Provide dual 120V UPS backed circuits to all meter enclosures. Refer to the BMS/DCIM section of this document for additional requirements. | TFO | Comply (part); Deviation (part); Exception (part) | Open | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. Compliance with, deviation from, or exception to "Meta PQM Performance Spec Rev 4" requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | PQM coordination can be part of TFO but expectation is LL is complying with spec. | Meta | 2 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
6 | Electrical | §B.a.i | Data Hall Server Row Power: 480/277V busways preferred (415/240V acceptable as alternative), lengths per rack layout. | TFO | Comply | Open | 480/277V power will not be provided. All server row power will be 415/240V. Row length and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Need feedback from Meta which is preferred, current plan is 480/415. | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
6 | Electrical | §B.a.iii | Data Hall Server Row Power: (1) Baseline Tap Box with dual L22-30R per rack position. Tap box layout to be reviewed/finalized during tenant fit out design development. | TFO | Comply | Closed | Tap-off box configuration, quantities, and locations will be determined as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Meta | 1 | Agreed, to be incorporated in to design during TFO | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.a.iii | Data Hall Server Row Power: Row busway to be rated 800A and fed from 100% rated 800A breaker (2x400A configuration acceptable as well). Busway size to be reviewed/finalized during tenant fit out design development. | Base Build | Comply | Open | Power Distribution Unit (PDU) output breakers which feed the row busways are currently 600AF/AT. All PDU output breakers will be changed to 800AF/AT, 3P, 100% rated breakers as part of Base Building scope of work. |  | Digital Realty | 1 | Are we (DLR) covering the PDU breaker swap cost? | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
7 | Electrical | §B.a.iv | Data Hall Server Row Power: Maximum available fault current to be 25KAIC at the server PSU input. Where 25KAIC is not achievable, Current-limiting fuse tap boxes must be used. | TFO | Comply | Closed | Tap-off box configuration, quantities, and locations will be engineered, furnished, and installed (EF&I) as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Meta | 1 | Agreed, to be incorporated in to design during TFO | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.a.v | Data Hall Server Row Power: Each row to have manual transition between primary and reserve power sources | TFO | Comply | Open | Each row will have manual transition between primary and reserve power sources located in the white space. Manual transfer switches (MTS's) will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 | No feedback from Meta, no disagreement from DLR to accommodate as part of the TFO process at Meta's cost. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.a.vi | Data Hall Server Row Power: Accessibility/maintenance: Busway horizontal access requirement is <2’ from front of the rack to the busway itself (not front of tap box). | TFO | Comply | Open | Power busway locations will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Assumed agreed, busway locations to be agreed to by Meta prior to install. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.a.vii | Data Hall Server Row Power: Each electrical distribution block shall never feed more than 2 data hall suites | Base Build | Comply | Assumed Closed | No comment. |  | Digital Realty | 1 | Assumed Closed, Each Suite Has Dedicated Infrastructure | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
7 | Electrical | §B.b.i | Reserve Connections: LL to provide a Reserve/catcher system. Each row has a manual transition to reserve; these connections may be daisy-chained such that one reserve switchboard is sufficient for all rows within a data hall. For all equipment serving more than one fault domain, the transition to reserve must be automatic. Intent is to be fully concurrently-maintable for all equipment serving more than one row, and fault tolerant for all equipment serving more than one failure domain. | Base Build (part); TFO (part) | Deviation | Open | Each PDU will have a reserve catcher system with automatic transfer switches (ATS's) as part of the Base Build. PDUs are concurrently maintanable. Manual transfer switches (MTS's) for each row can be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 | Require feedback from Meta | No response received from Meta. Digital Realty confirms deviation response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.c.i | UPS-Backed Ancillary Power: Provide dual 120V, 20A/1P, UPS backed circuits from diverse panels to meter enclosures. | TFO | Comply | Open | All equipment metering required per Meta PQM Performance Spec requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. This includes all CTs, PTs, branch circuit monitoring systems (BCMS), meters, meter enclosures, conduits & raceways, wiring, fixtures, fittings, hardware, 120VAC power, UPS systems, batteries, transformers, BMS/EPMS/DCIM interfacing, start-up, testing, programming, provisioning, and commissioning. |  | Meta | 1 | Assumed to be accepted as part of Meta TFO. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.c.ii | UPS-Backed Ancillary Power: Provide dual 230V, 20A/1P, UPS backed circuits from diverse panels to cold aisle goal post receptacles. | TFO | Comply |  | Dual 230V, 20A, 1P, UPS backed circuits from diverse panels will be provided to aisle goal post receptacles as part of Tenant Fit-Out (TFO) scope of work. Hot aisle containment (HAC) will be utilized in all data halls. | Why does this say DEVIATE? Should be comply. | Meta | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
7 | Electrical | §B.c.iii | UPS-Backed Ancillary Power: Provide dual UPS-backed power to all IDF racks | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
7 | Electrical | §B.d.i | Convenience Power: Cord reels (GFCI) or convenience receptacles are required to be accessible at every row. | TFO | Comply |  | Cord reels (GFCI) or convenience receptacles will be accessible at every row and will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
7 | Electrical | §B.e.i | Grounding: Provide (2) ground bars in each data hall. Refer to technology for requirements. | Base Build | Comply |  | A minimum of two (2) ground bars will be provided in each data hall. Ground bar size, configuration, and locations shall be as stated in Landlord's electrical drawings and specifications. | Will need to be coordinated with technology during TFO to ensure it meets requirements. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
7 | Electrical | §B.f.i | Transfer Inhibit: Landlord-provided transfer inhibits for each block redundant system to ensure the reserve system is not overloaded. Include capability to prevent automatic transfer in case a bypass procedure is being performed downstream. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
7 | Electrical | §B.g.i | Power System Study: For row level breakers, please ensure the minimum settings are such: 1. LTPU: Busway full load rating (example: 400A) 2. LTD: 12, I2T on (ensure within cable / busway thermal limits) 3. STPU: 2x LTPU 4. STD: 0.2, I2T off 5. Inst: 10x LTPU | TFO | Comply |  | Row level breaker settings will be programmed as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §B.g.ii | Power System Study: Ensure breakers upstream of row level coordinate with the settings above | TFO | Comply |  | Row level breakers will be fully coordinated with all upstream breakers as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
8 | Electrical | §C.a.i | Network System Row Power: (2) 415/240V dual UPS-backed busways in network suite. All remaining network busways to be single-corded, non-UPS-backed, 480/277V preferred (415/240V acceptable as alternative). Quantity of UPS backed rows to be reviewed/finalized during tenant fit out design development. | TFO | Comply |  | 480/277V power will not be provided. All network row power will be 415/240V and will be UPS backed. Quantity of rows, row length, and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §C.a.ii | Network System Row Power: Lengths per rack layout. | TFO | Comply |  | Quantity of rows, row length, and busway length will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §C.a.iii | Network System Row Power: Each busway to be rated 800A and powered from 800A, 100% rated breakers (2x 400A configuration acceptable as well). Busway size to be reviewed/finalized during tenant fit out design development. | Base Build | Comply |  | Power Distribution Unit (PDU) output breakers which feed the row busways are currently 600AF/AT. All PDU output breakers will be changed to 800AF/AT, 3P, 100% rated breakers as part of Base Building scope of work. |  | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
8 | Electrical | §C.a.iv | Network System Row Power: Tapboxes with dual L22-30R per rack position. Tap box type to match server areas. Quantities and locations per rack layout. | TFO | Comply |  | Tap-off box configuration, quantities, and locations will be determined as part of Tenant Fit-Out (TFO) scope of work. | Please note that tap boxes will need to be fused. To be coordinated during TFO. | Meta | 1 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §C.a.v | Network System Row Power: Accessibility/maintenance: Busway horizontal access requirement is <2’ from front of the rack to the busway itself (not front of tap box). Any larger distance requires further evaluation and alignment with Meta. | TFO | Comply |  | Power busway locations will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §C.b.i | Network System Grounding: Provide (2) ground bars in each space. Refer to technology for requirements. | Base Build | Comply |  | A minimum of two (2) ground bars will be provided in each data hall. Ground bar size, configuration, and locations shall be as stated in Landlord's electrical drawings and specifications. | Will need to be coordinated with technology during TFO to ensure it meets requirements. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
8 | Electrical | §D.a | Admin and DC Support Spaces: Refer to DSS for power and grounding requirements. | TFO | Comply |  | Any and all power and grounding for admin and data center support spaces will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §E.a | Lighting: Lighting to be LED; match landlord fixture types | Base Build (part); TFO (part) | Comply |  | Landlord is providing a baseline lighting design for the data halls as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline lighting package will be paid for by Meta as part of TFO NRCs. | N/A
8 | Electrical | §E.b | Lighting: Light levels to meet Meta standards in accordance with the DCC. | Base Build (part); TFO (part) | Comply |  | Landlord is providing a baseline lighting design for the data halls as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline lighting package will be paid for by Meta as part of TFO NRCs. | N/A
8 | Electrical | §F.a | Nameplates: All Meta equipment to have a nameplate that is legible from ground level | TFO | Comply |  | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §F.b | Nameplates: Nameplate to include at least the following information: i. Equipment Name ii. Fed from: iii. Source 1 and source 2 information (if applicable) | TFO | Comply |  | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements. |  | Meta | 1 | Digital Realty will follow Meta labeling schema, costs to be part of the TFO scope of work. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
8 | Electrical | §F.c | Nameplates: Examples shown below: | TFO | Comply |  | Nameplates for all Meta equipment will be provided as part of Tenant Fit-Out (TFO) scope of work. Nameplates for all Landlord equipment will comply with Landlord nameplate requirements. |  | Meta | 1 | Digital Realty will follow Meta labeling schema, costs to be part of the TFO scope of work. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
9 | Mechanical | §A.1 | Admin Offices and Support Spaces: Office/Support space cooling design to match Meta temperature and humidity standards as listed in the Data Center Space Standards (DCSS) document. | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to office space and support space cooling design requirements per Meta "Data Center Space Standards (DCSS)" document requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
9 | Mechanical | §A.2 | Admin Offices and Support Spaces: Size supplementary cooling/heating systems, if landlord’s air handler capacity is unable to meet office/support requirements, at design ambient ASHRAE conditions (0.4%cooling, 99.6% heating) | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
9 | Mechanical | §A.3 | Admin Offices and Support Spaces: Supplementary ventilation to be based on ASHRAE 62.1 | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
9 | Mechanical | §A.4 | Admin Offices and Support Spaces: Minimum admin space humidity of 30% RH | TFO | Comply |  | Cooling design for Office Space, Storage Spaces, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | Digital Realty will provide basic comfort cooling for office and storage spaces, further upgrades or enhancements may be made by Meta as part of the TFO process. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
9 | Mechanical | §B.1 | Studies and tooling: Development of rack loading based on site electrical distribution and review of landlord CFD (computational fluid dynamic) model to support Meta rack layout and temperature/humidity SLA requirements for all critical spaces. | TFO | Comply |  | Development of rack loading, rack location determination, and review of Landlord data hall CFD model(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
9 | Mechanical | §C.1 | Data Hall (Megapod)/Network Rooms: Provide infrastructure to support up to 100 percent (by power) air-cooling and up to an average of 80 percent (by power) liquid-cooling at the data hall level. At the individual row level technical water loops shall be sized to support 100 percent (by power) of the electrical busway capacity. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Noted that this has been agreed with the leasing team. | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §C.2 | Data Hall (Megapod)/Network Rooms: Front end network suites to be 100 percent (by power) air cooled day 1. Liquid cooling requirements for Front end network suites can be a deferred scope including CDU’s and piping. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 100% (by power) air-cooling at the data hall level will be provided for data halls designated as "Front End Network" data halls as part of the Base Building scope of work. Liquid cooling infrastructure within the data halls, including piping, for data halls designated as "Front End Network" data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. | Not a deviation but the liquid cooling for the FE space can be deferred, is there any benefit to deferring it or is it better to install now? | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §C.3 | Data Hall (Megapod)/Network Rooms: Any space noted as back end network suites shall mirror the data hall requirements. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Same as above. | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §C.4 | Data Hall (Megapod)/Network Rooms: The 100 percent/80 percent air-cooling/liquid-cooling infrastructure refers to cooling distribution systems inside the data halls (megapods) and network suites. Note that cooling demand can vary in any combination of 0 to 100 percent air-cooling and 0 to 80 percent liquid-cooling. | Base Build (part); TFO (part) | Comply |  | Infrastructure to support up to 85% (by power) air-cooling and up to 80% (by power) liquid cooling at the data hall level will be provided as part of the Base Building scope of work. Technical water loops sized to support 100% (by power) of the electrical busway capacity for each row will be provided as part of Tenant Fit-Out (TFO) scope of work. | Same as item 9 | Meta | 1 |  | Digital Realty response changed to "Comply". Back-of-house infrastructure will be paid for by Digital Realty as part of Base Build. Technical water loops will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.i | Rack-level waterside requirements: Maximum 86°F [30°C] supply water temperature. Typical operating temperatures of 80°F [27°C]. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.ii | Rack-level waterside requirements: 18°F ΔT [10°C ΔT] waterside rack ΔT. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.iii | Rack-level waterside requirements: Minimum 0.4 GPM / kW [1.5 LPM / kW] water flow rate. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.iv | Rack-level waterside requirements: 40 PSI ΔP [241-276 kPa ΔP] pressure drop across the rack. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.v | Rack-level waterside requirements: The technical water loop header needs to be sized to align with electrical distribution capacity for that row. I.e. The technical water loop needs to be sized to assume 100% of the server capacity in the row is water cooled. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.vi | Rack-level waterside requirements: 1-¼” drops at each rack position. Elevations and positions of drops to align with layouts drawings (provided as part of BoD Documents) | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.vii | Rack-level waterside requirements: Quick connects to be BSPP thread. Approved vendors: Parker, CEJN, Safeway | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.viii | Rack-level waterside requirements: Additional 3” drops at rack positions as shown in the diagram below for rows of up to 30 servers. For rows greater than 30 servers need to agree 3” drop locations with Meta on a case by case basis. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.ix | Rack-level waterside requirements: PG25 for the TW loop to be Dowfrost LC25. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.x.a | Rack-level waterside requirements, Cleanliness: Fill flush and treatment of TW loop shall meet Dow requirements for Dow LC25. Sample of water from the TW loop once construction is complete shall be sent to Dow for approval. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
10 | Mechanical | §D.1.x.b | Rack-level waterside requirements, Cleanliness: Landlord must guarantee that no solids greater than 25 micron in size shall pass through any of the liquid cooled servers. | TFO | Comply |  | Technical cooling system (TCS) infrastructure within the data halls will be provided as part of Tenant Fit-Out (TFO) scope of work. Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
11 | Mechanical | §D.2.i | Rack-level airside requirements: 65°F-85°F [18.3°C-29.4°C] supply air temperature. | Base Build | Comply |  | Airside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
11 | Mechanical | §D.2.ii | Rack-level airside requirements: 20%-80% supply air relative humidity, non-condensing. | Base Build | Comply |  | Airside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
11 | Mechanical | §D.2.iii | Rack-level airside requirements: 22°F ΔT [12.2°C ΔT] airside rack ΔT. | Base Build | Deviation |  | Airside SLAs will be as stated in Exhibit H of the Lease. Base Building design is 23°F ΔT. | Confirm what the impact would be of changing this to be 22F DT. ROM cost or schedule impact. | Digital Realty | 2 |  | Clarification needed from Meta: Exhibit H SLAs state 23°F ΔT, PDC requirements state 22°F ΔT. Which is correct? | Meta
11 | Mechanical | §D.2.iv | Rack-level airside requirements: 0.158 CFM / W [0.075 CMS / W] air flow rate. | Base Build | Deviation |  | Airside SLAs will be as stated in Exhibit H of the Lease. Base Building design is 147 cfm/kW. | Related to item above. | Digital Realty | 2 |  | Clarification needed from Meta: Exhibit H SLAs state 147 CFM/kW, PDC requirements state 158 cfm/kW. Which is correct? | Meta
11 | Mechanical | §D.2.v | Rack-level airside requirements: MERV 8 Recirculation Filters, MERV 13 OSA Filters | Base Build | Comply |  | Airside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
11 | Mechanical | §D.3.i | Cooling distribution units (CDUs): Concurrently maintainable, feeding into a looped or manifold piping arrangement (or equivalent). | Base Build | Comply |  | Waterside SLAs will be as stated in Exhibit H of the Lease. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
11 | Mechanical | §D.3.ii | Cooling distribution units (CDUs): UPS support for CDU’s is required. UPS time duration to match server shutdown time. This shall be 90 seconds or as required through discussions with the Meta server hardware team. | Base Build | Deviate |  | Waterside SLAs will be as stated in Exhibit H of the Lease. Mechanical UPS sizing and ride-through time are as required for Generator restart duration. | CDU UPS must be 5 minute minimum. | Digital Realty | 2 |  | Clarification needed from Meta: Requirement states 90-second UPS ride-through time, Meta Response comment states 5-minute UPS ride-through time. Which is correct? | Meta
11 | Mechanical | §D.4 | Liquid cooling infrastructure inside data halls and network rooms to independently support cooling failure domain, so that cooling failure does not impact more than one failure domain unless otherwise agreed with Meta. Landlords shall provide Meta alternative liquid cooling fault domain schemes with cost and schedule impacts for review. | Base Build | Comply |  | Each data hall has a dedicated cooling infrastructure such that any data hall level cooling failure does not affect any other data hall. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
11 | Architectural | §A.1.i.a | Programming & Circulation, Admin Office space: The first building on the campus will be the main building and need desk space for 35 employees. | TFO | Comply |  | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
11 | Architectural | §A.1.i.b | Programming & Circulation, Admin Office space: All subsequent buildings on the campus will require desk space for 20 employees. | TFO | Comply |  | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
11 | Architectural | §A.1.i.c | Programming & Circulation, Admin Office space: See “Open Office” in Meta Data Center Space Standards for configuration requirements. | TFO | Comply |  | Office/Storage Space area will be as stated in Section 1.3.(a) of the Lease and in locations as depicted in Exhibit B of the Lease. Office space construction, demising, fit-out, and furnishing will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Office/Storage Space configurations requirements per the "Open Office" section(s) of the Meta "Data Center Space Standards (DCSS)" document requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
11 | Architectural | §A.2.i | Programming & Circulation, Corridors and Pathway: Network Suites and Data Halls shall have an identified path of travel from the loading dock in which all building elements along the path can support the movement of Meta specified server racks and robotic tugs (Autonomour Guided Vehicles, or “AGV”) . Wall mounted objects (fire extinguishers, AEDs, etc) must be clear of the AGV path. | Base Build | Exception |  | A designated path-of-travel from the loading dock to the network suites and data halls will be established. Corridor width along the path-of-travel will be 8'-0" or greater. Doorway openings along the path-of-travel will be 6'-0" or greater. Certain wall mounted objects (fire extinguishers, AEDs, etc.) may protrude into the corridor and doors may swing out into the corridor. | Not accepted. Doorways along path of rack moves must be 8' wide by 9' high min. | Meta | 3 |  | Digital Realty will need to evaluate if it is possible to incease doorways along the path-of-travel to 8'-0" wide. | Dan Kingman
11 | Architectural | §A.2.ii.a | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Wall mounted objects (fire extinguishers, AEDs, etc) must be clear of the AGV path. | Base Build | Comply |  | Wall mounted objects (fire extinguishers, AEDs, etc.) will be installed in flush-mounted enclosures may protrude into the corridor. | Will these objected be outside of the 8' clear zone? If so, ok. If they protrude into the 8' zone then not accepted. | Digital Realty | 2 |  | Digital Realty response changed to "Comply". Corridor and pathway wall mounted objects shall be installed in flush mounted enclosures. Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
11 | Architectural | §A.2.ii.b | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Where possible, wall mounted objects should be consolidated on one side of the hallway. | Base Build | Comply |  | Wall mounted objects will be present on both sides of the corridor and will be installed in flush-mounted enclosures. | Will these objected be outside of the 8' clear zone? If so, ok. If they protrude into the 8' zone then not accepted. | Digital Realty | 2 |  | Digital Realty response changed to "Comply". Corridor and pathway wall mounted objects shall be installed in flush mounted enclosures. Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
11 | Architectural | §A.2.ii.c | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: Should be clear of temporary obstructions (door swings into corridors, temporary laydown storage, etc.). | Base Build | Exception |  | Doors will swing out into the corridors. | Ok. Safety signage will need to added in the area of door swing zone. | Digital Realty | 2 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Dan Kingman
12 | Architectural | §A.2.ii.d | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: If the corridor clear width is temporarily obstructed, operations must ensure an 8’-0” clear corridor during rack movements. | Base Build | Exception |  | It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors and adequate clearances prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Agree | Meta | 1 |  | Digital Realty confirms its exception and that no changes are required. | N/A
12 | Architectural | §A.2.ii.e | Programming & Circulation, Corridors and Pathway, Typical Corridor Width: If doors swing into the corridor, the corridor should be widened to allow for 8’-0” clear with the door open. | Base Build | Exception |  | Corridor widths are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Corridor widths are fixed and cannot be widened. | Ok. Safety signage will need to added in the area of door swing zone. | Digital Realty | 2 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | Dan Kingman
12 | Architectural | §A.2.iii | Programming & Circulation, Corridors and Pathway, AGV Types | Base Build | Exception |  | It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors and adequate clearances prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Agree | Meta | 1 |  | Digital Realty confirms its exception and that no changes are required. | N/A
12 | Architectural | §A.2.iv.a | Programming & Circulation, Corridors and Pathway, Freight Elevators: Located Centrally to IT Equipment Rooms and Loading Dock as possible. | Base Build | Deviation |  | Freight elevator locations are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Freight elevator locations are fixed and cannot be moved. | Accepted | Digital Realty | 1 |  | Digital Realty confirms its deviation and that no changes are required. | N/A
12 | Architectural | §A.2.iv.b | Programming & Circulation, Corridors and Pathway, Freight Elevators: Minimum of two per building; three is preferred | Base Build | Comply |  | The building has two (2) freight elevators. |  | Digital Realty | 1 |  | Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | N/A
12 | Architectural | §A.2.iv.c | Programming & Circulation, Corridors and Pathway, Freight Elevators: 15,000lbs. Weight capacity | Base Build | Deviation |  | Freight elevator weight capacity is 12,000 lbs. | Accepted. Confirm elevator is C rated. | Digital Realty | 2 |  | Digital Realty to confirm | Dan Kingman
12 | Architectural | §A.2.iv.d | Programming & Circulation, Corridors and Pathway, Freight Elevators: 9’ Minimum door height and 7’-3” opening width | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | N/A
12 | Architectural | §A.2.iv.e | Programming & Circulation, Corridors and Pathway, Freight Elevators: Interior cab dimensions min: 8’-4” width x 20-’10” depth and 9’-6” height. | Base Build | Deviation |  | Freight elevator cab depth is 9'-6" width x 10'-6" depth x 10'-0" height | Accepted | Digital Realty | 1 |  | Digital Realty confirms its deviation and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | N/A
12 | Architectural | §A.2.iv.f | Programming & Circulation, Corridors and Pathway, Freight Elevators: Provide wall-mirrors around elevators as a safety measure due to heavy PIV/pedestrian traffic and blind corners | TFO | Comply |  | Wall mirrors can be provided as part of Tenant Fit-Out (TFO) scope of work. | Why is this called out as a deviation? | Meta | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
13 | Architectural | §B.1 | Audio Visual: Office Spaces should follow Meta’s current AV Standard Designs. See Meta Data Center Space Standards. Refer to Standards Hub for information on lease programming in section 3a. | TFO | Comply |  | Audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
13 | Architectural | §B.1.i | Audio Visual: One Training room allowed per campus, no Multipurpose rooms are scoped for Meta lease campuses. | TFO | Comply |  | Training room(s), multiple purpose room(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
13 | Architectural | §B.1.ii | Audio Visual: One Meet Up space with either a single monitor @ 86” or three monitors @ 55” allowed per campus. In the event of multiple Meet up spaces within campus, The AV setup will only support procurement for one AV set up per campus. | TFO | Comply |  | Meet Up space(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
13 | Architectural | §B.1.iii.a | Audio Visual: Two wall-mounted monitors per set @ 55” in the Shipping & Receiving office (none in Loading Dock area) for AV dashboards | TFO | Comply |  | Shipping & Receiving office(s) and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
13 | Architectural | §B.1.iii.b | Audio Visual: EE service desk/helpdesk, IT vending machine, IT smart lockers, IT storage spaces | TFO | Comply |  | EE service desk(s)/helpdesk(s), IT vending machine(s), IT smart lockers, IT storage spaces and the associated audio visual items will be provided as part of Tenant Fit-Out (TFO) scope of work, space permitting. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
13 | Architectural | §C.1 | Room Numbering: All Meta dedicated rooms shall adhere to Meta Room Naming and Numbering Standards. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.2 | Room Numbering: If the landlord room numbering follows a different convention, both room numbers shall be provided on the drawings. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.3 | Room Numbering: Room numbers shall follow the guidance in the Meta Data Center Design Room Naming Standards. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.4 | Room Numbering: Ensure all spaces, including but not limited to the landlord owned spaces, are numbered, including roof areas. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.5 | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.5.i | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Meta-Owned MMR rooms shall be named MOMMR followed by a two digit designator. The MOMMR planned to route Path A/B (post 1) shall be MOMMR01 and the MOMMR planned to route Path C/D (post 2) shall be MOMMR02 | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.5.ii | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Point of Entry rooms shall be named POE followed by a two digit designator. POEs adjacent to MOMMRs shall share the same two digit designator as the MOMMR. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.5.iii | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Riser rooms shall be named RISER followed by a two digit designator. If the riser is included in the same room as an MOMMR or IDF room than the room shall use the MOMMR or IDF naming convention. The RISER planned to route Post 1 shall be named RISER01, and the RISER planned to route Post 2 shall be named RISER02. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
13 | Architectural | §C.5.iv | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: Admin IDF rooms shall be named ADMINIDF followed by a two digit designator. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
14 | Architectural | §C.5.iv | Room Numbering: Meta-Owned MMR rooms, Point of Entry, Riser rooms, Admin IDF, and GS IDFs rooms shall follow the following standards: General Service IDF rooms shall be named GSIDF followed by a two digit designator. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
14 | Architectural | §C.6 | Room Numbering: Ensure corridors are broken up as required to give each segment or turn a unique number. | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
14 | Architectural | §D.1 | Room Signage: Room signage shall comply with all code and local AHJ requirements. Room signage shall contain both landlord and Meta room numbering if different than Meta standard for all Meta leased spaces. | Base Build | Comply |  | Room signage will comply with all code and local AHJ requirements. Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work.and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Secondary/dual room names and numbers which adhere to Meta Room Naming and Numbering Standards can be added as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
14 | Architectural | §D.2 | Room Signage: META signage (placards) will only be used on all META occupied spaces and these additional landlord spaces: i. Electrical Rooms ii. UPS Rooms iii. Mechanical Galleries iv. House UPS Rooms | Base Build | Comply |  | Dual room naming and numbering will be utilized, following both Landlord and Meta Room Naming and Numbering Standards. Room naming and numbering will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's room naming and numbering standards. Adherance to Meta Room Naming and Numbering Standards will be determined as part of Tenant Fit-Out (TFO) scope of work. | Not accepted. Room naming for Meta occupied spaces will need to adhere to Meta standards. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
14 | Architectural | §E.1.i | Building Opening & Hardware, Door Hardware: Refer to Meta Data Center Requirements (2.1.3 Building Opening Planning & Guidelines) | TFO | Comply |  | Door hardware will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
14 | Architectural | §E.1.ii | Building Opening & Hardware, Door Hardware: Refer to the GDSS document for access control requirements. Meta security team to review for compliance with GDSS | TFO | Comply |  | Access control will be as detailed and shown in the Landlord's security drawings, plans, and specifications and will follow the Landlord's standards. Modifications to access control can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Security design must adhere to Meta requirements as outlined in the PDC. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
14 | Architectural | §E.2 | Building Opening & Hardware: Where vision panels are called out in design standards for doors, vision panels shall only be provided in interior Meta spaces, no vision panels in shared spaces. | Base Build | Comply |  | Certain common area spaces, such as conference rooms, breakout rooms, and break rooms, have doors with vision panels or glass doors and walls. | Please further clarify deviation. | Digital Realty | 1 |  | Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | N/A
14 | Architectural | §E.3.i | Building Opening & Hardware, Doors: All doors along the rack path shall receive automatic operator and security hardware. | TFO | Comply |  | Doors along the rack path are manually operated and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door operation and hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
14 | Architectural | §E.3.ii | Building Opening & Hardware, Doors: Doors shall open the maximum extent possible and shall be double doors 8’-0” x 9'-0”. | Base Build | Deviation |  | Double doors along the rack path are 6'-0" wide x 9'-0" high and will open to the maximum extent possible. | Not accepted. Doorways along path of rack moves must be 8' wide by 9' high min. |  | 3 |  | Digital Realty to investigate | Dan Kingman
14 | Architectural | §E.3.ii.a | Building Opening & Hardware, Doors: Controlled double doors into equipment rooms required for movement of loaded racks from docks for installation in equipment areas with adequate clearance to safely maneuver by the robotic tugs. | TFO | Comply |  | Doors along the rack path are manually operated and will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door operation and hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. It is the responsibility of Tenant and Tenant's operations team to ensure clear corridors, adequate clearances, and proper door operation (opening) prior to and during rack movements. Tenant is solely responsible for all rack movements, the safety thereof, and the proper and safe use of automatic guided vehicles (AGVs). | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
14 | Architectural | §E.3.iii.a | Building Opening & Hardware, Doors, Door Hardware: Lock and latch sets, including electrified, to be heavy duty commercial mortise type | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
14 | Architectural | §E.3.iii.b | Building Opening & Hardware, Doors, Door Hardware: Use electric strikes only on aluminum/glass entrance doors as a last resort | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
14 | Architectural | §E.3.iii.c | Building Opening & Hardware, Doors, Door Hardware: Provide key override at each electric strike and electrified lock set | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
14 | Architectural | §E.3.iii.d | Building Opening & Hardware, Doors, Door Hardware: Use push pad style exit devices where required to satisfy code or local jurisdiction requirements | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
14 | Architectural | §E.3.iii.e | Building Opening & Hardware, Doors, Door Hardware: All lock cylinders shall be MEDECO High Security | TFO | Comply |  | Door hardware and lock cylinders will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware and lock cylinders can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
14 | Architectural | §E.3.iii.f | Building Opening & Hardware, Doors, Door Hardware: Lever sets: heavy-duty mortise hardware | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §E.3.iii.g | Building Opening & Hardware, Doors, Door Hardware: Hinges: stainless steel heavy duty mortised butt-hinges in accordance with manufacturer’s recommendations at swing doors | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §E.3.iii.h | Building Opening & Hardware, Doors, Door Hardware: Hinges to be tamper-resistant (NRP) throughout | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §E.3.iii.i | Building Opening & Hardware, Doors, Door Hardware: Flush bolts/coordinators on all pairs with an inactive leaf | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §E.3.iii.j | Building Opening & Hardware, Doors, Door Hardware: Closers: heavy duty hydraulic | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §E.3.iii.k | Building Opening & Hardware, Doors, Door Hardware: Provide seals for weather tightness and sound dampening | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §E.3.iii.l | Building Opening & Hardware, Doors, Door Hardware: Panic hardware: as required by code and at electrical rooms | TFO | Comply |  | Panic hardware will be provided and installed as required by code. Door hardware will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's standards. Modifications to door hardware can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
15 | Architectural | §E.3.iii.m | Building Opening & Hardware, Doors, Door Hardware: All doors to receive REX unless otherwise indicated | TFO | Comply |  | Door functionality allows for free egress at all times. Modifications to door functionality can be made as part of Tenant Fit-Out (TFO) scope of work, if feasible. | Not accepted. Door hardware for Meta occupied space must adhere to Meta standards, and be in line with Meta security and robotics integration requirements. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
15 | Architectural | §E.3.iii.n | Building Opening & Hardware, Doors, Door Hardware: EOR responsibility to ensure all hardware is fully compatible with the door manufacturer and meets all building codes | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
15 | Architectural | §F | Meta Lighting Requirements: Includes table listing (19) space types and their associated illimination requirements. | Base Build (part), TFO (part) | Deviation |  | Landlord is providing a baseline lighting design for all spaces as of the Effective Date of the Lease. Moves, adds, changes, or reconfigurations to Landlord's baseline lighting layout and design, including coordination with Tenant's rack & row layouts and with other overhead services to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. All lighting for Tenant leased Office Space, Storage Space, and Ancillary Space(s) to meet Tenant illumination requirements will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline lighting package will be paid for by Meta as part of TFO NRCs. | N/A
15 | Architectural | §G.1 | Interior Construction & Materials: Interior partitions shall receive code required fire and smoke wall ratings in addition to minimum 1-hour fire and smoke rated construction between the computer equipment rooms and office areas, between computer equipment rooms and electrical rooms, and around MPOE/BDF rooms, except where greater rating is required by code. | Base Build (part); TFO (part) | Deviation |  | Interior partitions are as detailed and shown in the Landlord's architectural drawings, plans, and specifications. Changes or reconfigurations, including changes in fire ratings, to interior partitions will be provided as part of Tenant Fit-Out (TFO) scope of work, if feasible. All partitions for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline construction package will be paid for by Meta as part of TFO NRCs. | N/A
16 | Architectural | §G.1.i | Interior Construction & Materials: See Meta Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines) | Base Build (part); TFO (part) | Deviation |  | Materials and acoustic properties are as detailed and shown in the Landlord's architectural drawings, plans, specifications, and basis of design. Changes in materials, acoustic properties, or compliance with Meta "Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines)" will be provided as part of Tenant Fit-Out (TFO) scope of work, if feasible. All materials, acoustic properties, and compliance with Meta "Data Center Requirements for Acoustic Guidelines (2.1.5 Building Acoustic Guidelines)" for Tenant leased Office Space, Storage Space, and Ancillary Space(s) will be provided as part of Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline construction package will be paid for by Meta as part of TFO NRCs. | N/A
16 | Architectural | §G.2.i | Interior Construction & Materials, Ceiling: A structural ceiling system shall be provided in all data halls and network rooms meeting the loading requirements. The strut ceiling grid shall be braced to control sway from interior air flow and floats around the perimeter to avoid transferring forces into interior or exterior partitions. | Base Build (part), TFO (part) | Deviate |  | Base building Structural Ceiling Grid to be provided. Meta required hanging loads to be analyzed and modified as required as part of the Tenant Fit-Out (TFO) scope of work. | Accepted | Meta | 1 |  | Digital Realty confirms its deviation response and that no changes are required. Any modifications to Landlord's baseline structural ceiling grid will be paid for by Meta as part of TFO NRCs. | N/A
16 | Architectural | §G.2.ii | Interior Construction & Materials, Ceiling: All areas containing food service (FS) equipment must have a finished ceiling installed overhead | TFO | Comply |  | Food services design, build-out, and construction administration services will not be provided by Landlord. | Not accepted. We will need to have a microkitchen put in the admin space. | Meta | 2 |  | Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
16 | Architectural | §G.3 | Interior Construction & Materials: Hot Aisle Containment shall allow for racks up to 8’-0” in height. Ensure airflow is blocked in the gap between racks and bottom of containment while allowing containment to move up and down slightly. Infill panels shall be provided for 10% of rack positions. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
16 | Architectural | §G.4 | Interior Construction & Materials: Review flatness & weight capacity criteria for robotics & servers with Meta | Base Build | Comply |  | Flatness and floor loading capacity will be as detailed and shown in the Landlord's structural drawings, plans, specifications, and basis of design. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | N/A
16 | Architectural | §G.5 | Interior Construction & Materials: Ceilings - No Meta-specific loading criteria. Design and construct in accordance with applicable local building codes, regulations, and industry standards. | Base Build | Comply |  |  |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of the Base Build. | N/A
16 | Architectural | §H.1 | Furniture: All Furniture in Meta spaces is OFOI. AV scope must be closely coordinated with the Meta Furniture team for conference room integration. | TFO | Comply |  | All furniture and AV items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO. | Dan Kingman
16 | HAC Design | §I.1 | Rack Height Accommodation and Airflow: Hot Aisle Containment shall allow for racks up to 8'-0" in height. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
16 | HAC Design | §I.2 | Rack Height Accommodation and Airflow: Ensure airflow is blocked in the gap between racks and the bottom of containment while allowing containment to move up and down slightly. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
16 | HAC Design | §I.3 | Rack Height Accommodation and Airflow: Where IT equipment is not installed, or is not of a consistent height, an adjustable blanking panel(s) shall be provided to achieve a positive seal to mitigate air loss from the HAC. | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
16 | HAC Design | §I.3.i | Rack Height Accommodation and Airflow: Sliding HAC panels shall be provided to access the cable pathways | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
16 | HAC Design | §J.1 | Aisle Layout and Clearance: Hot aisles: 6 feet with 5 feet clear | TFO | Comply |  | Hot aisle width and clearances will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
16 | HAC Design | §J.2 | Aisle Layout and Clearance: Cold aisles: 14 feet with 7 feet clear | TFO | Comply |  | Cold aisle width and clearances will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
16 | HAC Design | §J.3 | Aisle Layout and Clearance: Ensure adequate clearance between HAC columns and adjacent racks to allow for easy maintenance and access | TFO | Comply |  | Precise clearances between HAC columns and adjacent racks will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
16 | HAC Design | §K.1 | HAC System Design and Interface: Connection, panel, and construction details of the containment interface should be designed to accommodate various rack heights within a row | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
16 | HAC Design | §K.2 | HAC System Design and Interface: The TORC system should be designed to accommodate different rack heights within a row | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
17 | HAC Design | §L.1 | Safety and Code Compliance: HAC systems should be designed to meet seismic design requirements to ensure stability and integrity during earthquakes | TFO | Comply |  | Hot aisle containment (HAC) system will be designed and constructed to meet local seismic criteria and will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
17 | HAC Design | §L.2 | Safety and Code Compliance: HAC systems should be constructed using fire-resistant materials to minimize the risk of fire spread | TFO | Comply |  | Hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
17 | HAC Design | §L.3 | Safety and Code Compliance: All necessary grounding between LV racks and equipment to be provided | TFO | Comply |  | Grounding for LV racks, equipment, and hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
17 | HAC Design | §M.1 | Labeling and Identification: Installing Row Position Labels in Production Rows and Row-End Labels denoting each row per design on both ends above HAC doors | TFO | Comply |  | Row position labels, row end labels, and hot aisle containment (HAC) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
17 | Controls & DCIM | §A.1 | System Overview: The leased facility incorporates two distinct and independently managed networks: the Landlord's operational network and Meta's dedicated Facilities Network (FacNet) | TFO | Comply |  | Installation of Meta's dedicated Facilities Network (FacNet) will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
17 | Controls & DCIM | §B.1 | Landlord Owned Equipment: The control and monitoring of landlord mechanical and electrical equipment and the corresponding Building Management System (BMS) / Electrical Power Monitoring System (EPMS) shall be owned, operated and maintained by the Landlord. This should be developed in the base build scope of work. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
17 | Controls & DCIM | §B.2 | Landlord Owned Equipment: The landlord shall allow for Web access (READ – ONLY) to Meta users to access both the landlords BMS and EPMS. | Base Build | Comply |  | Access to Landlord's BMS and EPMS will be provided via web portal and via API(s). |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Ryan Young
17 | Controls & DCIM | §C.1 | Meta FacNet and Data Center Infrastructure Management (DCIM): Integration with Meta's DCIM system will involve monitoring all specified electrical parameters to meet both Dynamo and line of demarcation requirements. Additionally, it will monitor critical environmental conditions within essential spaces to ensure compliance with Service Level Agreements (SLAs). | TFO | Comply (part); Deviation (part); Exception (part) |  | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to monitoring all specified electrical parameters to meet Dynamo and line of demarcation requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
17 | Controls & DCIM | §C.1.i | Meta FacNet and Data Center Infrastructure Management (DCIM): Note: Dynamo is a real-time power monitoring and protection reliability system that protects Meta’s power distribution network from power overages, spikes, and unplanned power surges. | TFO | Comply (part); Deviation (part); Exception (part) |  | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to monitoring all specified electrical parameters to meet Dynamo and line of demarcation requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
17 | Controls & DCIM | §C.2 | Meta FacNet and Data Center Infrastructure Management (DCIM): Each DCIM monitoring point and alert must be thoroughly tested and verified through the DCIM tooling with Ignition. | TFO | Comply (part); Deviation (part); Exception (part) |  | Integration with Meta's DCIM system will be provided as part of Tenant Fit-Out (TFO) scope of work. Compliance with, deviation from, or exception to Meta DCIM monitoring point and alerting testing and verification requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
17 | Controls & DCIM | §C.3 | Meta FacNet and Data Center Infrastructure Management (DCIM): DCIM integration point naming must align with DCIM naming standards (BMS-PLAN-348 – FDM Playbook Rev 1.0). | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | DCIM integration point naming will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's BMS and EPMS point naming and numbering standards. Compliance with, deviation from, or exception to dual naming, re-naming, or aligning with Meta DCIM naming standards per BMS-PLAN-348 - FDM Playbook Rev 1.0 will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
17 | Controls & DCIM | §C.3.i | Meta FacNet and Data Center Infrastructure Management (DCIM): If LL equipment naming differs from DCIM integration point naming, label containing DCIM point name is to be provided on equipment being integrated. | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | DCIM integration point naming will be as detailed and shown in the Landlord's architectural drawings, plans, and specifications and will follow the Landlord's BMS and EPMS point naming and numbering standards. Compliance with, deviation from, or exception to providing equipment labeling with DCIM, BMS, or EPMS point name will be determined as part of Tenant Fit-Out (TFO) scope of work. | [BW] Acceptable to be determined at Tenant Fit Out | Meta | 1 |  | Digital Realty confirms its response and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
17 | Controls & DCIM | §C.4.i | Electrical Monitoring - DCIM: Meta dedciated Power Quality Meters (PQM's) for Landlord owned MSB's. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
17 | Controls & DCIM | §C.4.i.a | Electrical Monitoring - DCIM: Separate meter enclosure shall be furnished with a monitored tamper switch. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.4.i.b | Electrical Monitoring - DCIM: PQM to be wired (Modbus RS485) to a Meta dedicated gateway panel located within Meta space. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.4.i.c | Electrical Monitoring - DCIM: Gateway panel shall connect directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.4.ii | Electrical Monitoring - DCIM: Meta dedciated PQM for Landlord PDU (Power Distribution Unit) (or equivalent line of demarcation) with branch circuit monitoring for row level metering. | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.4.ii.a | Electrical Monitoring - DCIM: PDU's will follow the same physical and network security requirements as MSB PQM (e.g., separate enclosure and wired to gateway panel) unless meter brick is located within Meta secure space, in which case it can connect direct to Meta’s facility network (FacNet). | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.4.ii.b | Electrical Monitoring - DCIM: Modbus TCP/IP integration to Meta’s facility network (FacNet). | TFO | Comply |  | Meta dedicated PQM's and associated enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.i | Mechanical Monitoring - DCIM: Data Hall | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.i.a | Mechanical Monitoring - DCIM: Temperature and Humidity monitoring for every cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.i.a.1 | Mechanical Monitoring - DCIM: Instruments to be provided with magnet backing and sufficient cable slack to allow placement at any rack position in the cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.i.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the data hall. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.i.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.i.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.ii | Mechanical Monitoring - DCIM: Network Core Room/s | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.ii.a | Mechanical Monitoring - DCIM: Temperature and Humidity monitoring for every cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.ii.a.1 | Mechanical Monitoring - DCIM: Instruments to be provided with magnet backing and sufficient cable slack to allow placement at any rack position in the cold aisle. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.ii.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the room. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.ii.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.ii.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii | Mechanical Monitoring - DCIM: Technical Water | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a | Mechanical Monitoring - DCIM: The following is to be monitored: | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Supply Water Temperature | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Return Water Temperature | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Differential Pressure | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.a.1 | Mechanical Monitoring - DCIM: Flow Rate | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.b | Mechanical Monitoring - DCIM: Devices to be wired (Modbus RS485) to a Meta gateway panel located centrally within the data hall. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
18 | Controls & DCIM | §C.5.iii.c | Mechanical Monitoring - DCIM: Gateway panel connects directly via Modbus TCP/IP to Meta’s Facility Network (FacNet). | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
19 | Controls & DCIM | §C.5.iii.d | Mechanical Monitoring - DCIM: Alarm thresholds to be set within SLA requirements defined by lease agreement. | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
19 | Controls & DCIM | §C.5.iv | Mechanical Monitoring - DCIM: Cooling Distribution Units (where applicable) | TFO | Comply |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
19 | Controls & DCIM | §C.5.iv.a | Mechanical Monitoring - DCIM: The CDUs shall be monitored and controlled (where applicable) by the landlords BMS. | TFO | Comply (part); Deviation (part) |  | Meta dedicated mechanical monitoring sensors and associated housings, fittings, enclosures, raceway, wiring, ancillary devices, and supporting items will be provided as part of Tenant Fit-Out (TFO) scope of work. The Landlord BMS will monitor and report on CDU operation; however, CDU control will be via separate controllers and control network (top-level Landlord BMS is 'observe and report' only). | [BW] Please confirm control of CDU is done by the landlord regardless if it's a separate controller and/or network. Meta will not be controlling the CDUs. | Meta | 1 |  | Confirmed, Digital Realty will operate the CDUs. Digital Realty confirms our response and that no changes are required. Item will be paid for by Meta as part of the TFO | Ryan Young
19 | Controls & DCIM | §C.6.i | Meta FacNet Security: Meta requires that all products, equipment, systems, components, and subcomponents comply with strict network compatibility and security requirements. Devices must be reviewed and approved by submitting Exhibit L, which includes detailed compliance forms such as the Product Compliance Form, Communications System Compliance Form, Component Compliance Form, and supporting documentation like communication diagrams and product data sheets. This submission ensures that devices meet Meta's network and security standards before approval for use. | TFO | Comply |  | Landlord will submit Exhibit L forms as required for Meta's review and approval. Submission of the Exhibit L forms and compliance with, deviation from, or exception to Meta's requirements will be determined as part of Tenant Fit-Out (TFO) scope of work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of the TFO | Dan Kingman
19 | Security | §A.a | General: Physical security, including guard force, operational policies/procedures, access controls, badging, intrusion detection and video surveillance will be the primary responsibility of the Landlord, unless otherwise noted in the lease. | Base Build | Comply |  | No comment. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that security is a Landlord responsibility and will be provided as part of the Base Build. Compliance with, deviation from, or exception to specific requirements in the "Security" will be stated for each individual requirement. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Jason Brunen
19 | Security | §A.b | General: All security requirements within this document, with the exception of those installed as part of the Meta fit out, are required at lease commencement. Any exceptions must be reviewed and approved by Meta. | Base Build | Comply |  | Compliance with, deviation from, or exception to any Meta Security requirements for each Program Design Criteria (PDC) section, subsection, or line item is as stated below. Installation of equipment to support each PDC security requirement will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty response changed to "Comply". Digital Realty confirms that it will review security requirements with Meta. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Jason Brunen
19 | Security | §A.c | General: Security requirements that are part of the Meta Fit Out are required to be active before Meta Fit out completion. | TFO | Comply |  | Compliance with, deviation from, or exception to any Meta Security requirements for each Program Design Criteria (PDC) section, subsection, or line item is as stated below. Installation of equipment to support each PDC security requirement will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty response changed to "Comply". Digital Realty confirms that it will review security requirements with Meta. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Jason Brunen
19 | Security | §B.a | Compliance: The landlord shall comply with the latest ISO/IEC 27001 Information Technology -Security Techniques - Information Security Management Systems - Requirements. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
19 | Security | §B.b | Compliance: The Landlord shall comply and provide evidence of compliance and certification on an annual basis. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
19 | Security | §B.c | Compliance: The Landlord shall comply and provide evidence of compliance with the SOC2 Standards on an annual basis. | Base Build | Comply |  | The initial evidence of compliance (SOC2 report) will be provided once the facility has been in operation for one (1) full calendar year (e.g., if the facility is completed in October 2026, the initial SOC2 report will be for 2027 and will be provided in 2028). Landlord can provide bridging letters as required by Tenant. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
19 | Security | §C.a | Submittals: The Landlord shall provide project design drawings, specifications and commissioning reports to Meta for review and comment throughout the design and construction process to ensure compliance with the security requirements included in the Lease Agreement. | Base Build (part), TFO (part) | Comply |  | Submittals for security related items for the Base Build scope-of-work will be provided by Landlord. Submittals for security related items for the Tenant Fit-Out (TFO) scope-of-work will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Landlord reserves the right to reasonably redact submittal information to the degree that it does not impact Meta's ability to evaluate for compliance to requirements. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
20 | Security | §C.a | Coordination & Inspections: Landlord shall communicate the following non-design & design related information to Meta Security prior to the design kick off date: i. Team member roles & responsibilities. ii. Paths of escalation. iii. Distribution Lists for drawing packages. iv. Security BoD (Basis of Design) or Building Security Narrative. v. List of Landlord approved security devices to be deployed (model/ part number, etc…) | Base Build (part), TFO (part) | Comply |  | Information for security related items for the Base Build scope-of-work will be provided by Landlord. Information for security related items for the Tenant Fit-Out (TFO) scope-of-work will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Landlord reserves the right to reasonably redact submittal information to the degree that it does not impact Meta's ability to evaluate for compliance to requirements. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
20 | Security | §C.b | Coordination & Inspections: During design, Landlord shall ensure that all information communicated to Meta Security for general coordination (e.g., design drawings, specifications, security device selection & installation/commissioning, construction schedules, supporting infrastructure, space hand-over dates, etc.) are based on the most recent version of the design to facilitate efficient coordination between Security, Meta’s design teams, and the landlord’s security designer. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
20 | Security | §C.c | Coordination & Inspections: If Meta fitout security designer differs from base build security designers, ensure coordination between security design occurs. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
20 | Security | §C.d | Coordination & Inspections: During construction, regular fortnightly coordination meetings beginning at least two months ahead of planned security go live dates, to coordinate site and space access, space lockdown and other items. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
20 | Security | §C.e | Coordination & Inspections: Meta Security requests to conduct a minimum of two site observations during construction to ensure scope is being executed correctly in accordance with the contract documents. These will generally occur prior to base-build security completion and Meta fit out security completion. Prior to the observations occurring, Meta Security will communicate the dates & associated agendas for each walk at least 30 days prior to it occurring. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
20 | Security | §D.a | Environmental Design and Construction: Telecommunications Vaults | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | See comments to §D.a.i and §D.a.ii, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dan Kingman
20 | Security | §D.a.i | Environmental Design and Construction: All telecommunication vaults, on data center property, shall be located within security perimeter fence line and physically secured by the landlord to prevent unauthorized access (e.g., lockable bolt, lockable cover, padlock) | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dan Kingman
20 | Security | §D.a.ii | Environmental Design and Construction: Subject to Meta review and approval, telecommunication vaults located outside the secure perimeter, shall be locked and alarmed to detect intrusion. | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dan Kingman
20 | Security | §D.b | Environmental Design and Construction: Fence | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
20 | Security | §D.b.i | Environmental Design and Construction: A secure perimeter around the property shall be provided including a physical barrier to restrict access by pedestrians and vehicles (e.g., fence) and one or more secure entrances to provide vehicle and pedestrian access through the secure perimeter. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
20 | Security | §D.b.ii | Environmental Design and Construction: The fence shall contain no person-passable openings, except those required for any secure entries, and reasonably restrict access by climbing by maintaining a minimum height above grade of 8 feet with an anti-climb topper. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.b.iii | Environmental Design and Construction: The fence shall contain no person-passable openings, except those required for any secure entries, and reasonably restrict access by climbing by maintaining a minimum height above grade of 8 feet with an anti-climb topper. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.c | Environmental Design and Construction: Site Entrance | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.c.i | Environmental Design and Construction: Secure entries shall allow for verification of business need for all access by personnel, pedestrians or in vehicles prior to permitting access through the secure perimeter. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.c.i | Environmental Design and Construction: Secure entries shall utilize access control and video surveillance systems to document site access and provide a historic record for investigations. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.d | Environmental Design and Construction: Building Requirements | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.d.i | Environmental Design and Construction: A continuous secure envelope around Meta’s Leased Space including walls, doors, and access points (including below raised floors and above drop ceilings) shall be provided. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.d.ii | Environmental Design and Construction: All Landlord equipment, support spaces, network infrastructure support spaces (e.g., MDF, BDF, etc.), and electrical infrastructure support space shall be physically separated from the Meta’s leased space. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.d.iii | Environmental Design and Construction: The Landlord shall provide secure cages within Meta space to separate General System Racks from Production Racks. Cage design shall be in accordance with Meta’s requirements. | TFO | Comply |  | Secure cages within Meta spaces, if required, will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §D.d.iv | Environmental Design and Construction: Meta’s Production Network gear which performs fabric aggregation functions shall be located within the Network Suite or GS.MDF and be physically separated from the data hall. Meta to advise during design. | TFO | Comply |  | Any work required to physically separate Meta's production network gear from the data hall will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.a | Secured Cage or Mesh Wall Requirements: General | TFO | Comply |  | See comments to §E.a.i, §E.a.ii, and §E.a.iii, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.a.i | Secured Cage or Mesh Wall Requirements: Secure cages/mesh walls are used to physically partition spaces within data centers to restrict physical access to a space (e.g. IDF, etc.) | TFO | Comply |  | Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.a.ii | Secured Cage or Mesh Wall Requirements: When required, they shall not impede airflow or equipment operation. Impact on airflow and cooling shall be considered in the design. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.a.iii | Secured Cage or Mesh Wall Requirements: Adhere to required clearances to adjacent equipment, exit paths, doorways, rack pathways, and other equipment. | TFO | Comply |  | Landlord will adhere to code-required clearances as part of the Base Build scope-of-work. Accommodation for specific clearances required by Meta will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.b | Secured Cage or Mesh Wall Requirements: Design Requirements | TFO | Comply |  | See comments to §E.b.i, §E.b.ii, §E.b.iii, and §E.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.b.i | Secured Cage or Mesh Wall Requirements: Secure cages shall be at least 8’ AFF or the height required for rack height, but not higher than tier 3 tray. | TFO | Comply |  | Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.b.ii | Secured Cage or Mesh Wall Requirements: The cage shall be constructed from wire mesh panels attached to posts. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.b.iii | Secured Cage or Mesh Wall Requirements: The maximum gap between the bottom of the mesh panel and the floor below shall be 2 inches. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.b.iv | Secured Cage or Mesh Wall Requirements: If required, provide a screen or fabric attached to mesh for visual privacy. | TFO | Comply |  | Any privacy screens or panels required will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.c | Secured Cage or Mesh Wall Requirements: Material | TFO | Comply |  | See comments to §E.c.i and §E.c.ii, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
21 | Security | §E.c.i | Secured Cage or Mesh Wall Requirements: Wire Mesh: 1”x1” powder coated black wire mesh; 9-gauge (minimum) | TFO | Comply |  | Base Building cage or mesh wall wire mesh will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall wire mesh requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any wire mesh for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.c.ii | Secured Cage or Mesh Wall Requirements: Posts: 2”x2” post anchored to concrete slab or raised access floor (as applicable). If the cage is on a raised floor, then there is no need to extend below the raised floor. | TFO | Comply |  | Base Building cage or mesh wall support posts will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall support post requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any support posts for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.d | Secured Cage or Mesh Wall Requirements: Doors | TFO | Comply |  | See comments to §E.d.i, §E.d.ii, and §E.d.iii, below. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.d.i | Secured Cage or Mesh Wall Requirements: All doors shall be wire-mesh doors with electrified hardware, door actuators, and applicable access control, and door position switch. Strobes and sounders may be installed at the behest of the landlord, Meta Security takes no exception to the installation of these devices. | TFO | Comply |  | Base Building cage or mesh wall doors and access control will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door and access control requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any doors and access control for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.d.ii | Secured Cage or Mesh Wall Requirements: Secure cage door hinges shall be located on the interior (secure) side or utilize tamper- resistant hardware. | TFO | Comply |  | Base Building cage or mesh wall door hinges and hardware will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door hinge and hardware requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.d.iii | Secured Cage or Mesh Wall Requirements: Secure cage doors shall be designed to prevent manipulation of interior (secure side) hardware from the exterior (unsecure side). A typical method is through incorporating anti-tamper steel sheeting to mitigate the risk of manipulation of door hardware from the non-secure side. | TFO | Comply |  | Base Building cage or mesh wall door hardware and trim will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta cage and mesh wall door hardware and trim requirements can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any door hardware and trim for secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Scope changed to Tenant Fit-Out (TFO) scope-of-work. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.e | Secured Cage or Mesh Wall Requirements: Video Surveillance | Base Build (part), TFO (part) | Comply |  | See comments to §E.e.i and §E.e.iii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.e.i | Secured Cage or Mesh Wall Requirements: Cameras shall provide ID level video coverage at both card readers as per video surveillance requirements section. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance of cage or mesh wall ingress and egress locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta video surveillance requirements for cage or mesh wall ingress and egress locations can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any video surveillance of secure cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §E.e.ii | Secured Cage or Mesh Wall Requirements: Security cabling shall be contained within the caged area. | Base Build (part), TFO (part) | Comply |  | Base Building security cabling for cage or mesh wall ingress and egress locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Compliance with Meta security cabling requirements for cage or mesh wall ingress and egress locations can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. Any security cabling for cages required to physically partition spaces within Meta leased areas or otherwise restrict access to Meta equipment will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §F.a | Loading dock: The loading dock shall be considered shared Meta space in which the Landlord will be responsible for providing, managing, and maintaining all aspects of the following security measures within the space, including as a minimum (i) Access Control System, (ii) Video Monitoring System. | Base Build | Comply |  | Base Building access control and video monitoring for the loading dock will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control or video monitoring systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §F.b | Loading dock: There shall be Landlord provided, managed, and maintained overview-level video coverage of the exterior of the loading dock. | Base Build | Comply |  | Base Building video monitoring for the loading dock will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video monitoring systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
22 | Security | §F.c | Loading dock: Meta shall always have reasonable access to a loading dock and a freight elevator at all times (in common with other tenants of the Building), subject to the Building Rules and Regulations. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | N/A
22 | Security | §F.d | Loading dock: Doors from the exterior into the loading dock shall be secured by the Landlord using 2-factor access control. | Base Build | Comply |  | Landlord's standard Base Building access control from the exterior into the loading dock is via card reader. Two-factor authentication (card-key plus biometric) can will be provided as part of the Tenant Fit-Out (TFO) Base Build scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | N/A
22 | Security | §G.a | Access Control: General | Base Build | Comply (part); Deviation (part); Exception (part) |  | See comments to §G.a.i through §G.a.vi, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that security is a Landlord responsibility and will be provided as part of the Base Build. Compliance with, deviation from, or exception to specific requirements in the "Security" will be stated for each individual requirement. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Jason Brunen
22 | Security | §G.a.i | Access Control: The Landlord shall be responsible for providing, managing, and maintaining all aspects of the access control system for the entire Data Center, including within Meta leased space. This includes all cabling, pathways, rough-in, and devices for all access controlled doors. | Base Build | Comply |  | Base Building access control will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that security is a Landlord responsibility and will be provided as part of the Base Build. Compliance with, deviation from, or exception to specific requirements in the "Security" will be stated for each individual requirement. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Jason Brunen
22 | Security | §G.a.ii | Access Control: All exterior doors into the Data Center shall be access-controlled by the Landlord. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
23 | Security | §G.a.iii | Access Control: The Landlord shall not traverse Meta leased space to access other Landlord space (electrical rooms, etc.) | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
23 | Security | §G.a.iv | Access Control: There shall be no designated path of egress from landlord/common space through Meta leased space, unless unavoidable and required by the AHJ and approved by the Meta. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
23 | Security | §G.a.v | Access Control: There shall be no exterior doors that lead directly into Meta leased space unless unavoidable and required by the AHJ and approved by the Meta. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
23 | Security | §G.a.vi | Access Control: Access control system shall adhere to OSDP version 2.2 or latest version | TFO | Comply (part); Deviation (part); Exception (part) |  | Compliance with, deviation from, or exception to access control system requirements per OSDP version 2.2 or the latest version will be determined as part of Tenant Fit-Out (TFO) scope-of-work. Installation of access control system equipment to support each particular requirement of OSDP version 2.2 or the latest version will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty will review the OSDP version 2.2 requirements with Meta to determine compliance with, deviation from, or exception to specific requirements within the document. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
23 | Security | §G.b | Access Control: Meta Lease Space | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | See comments to §G.b.i through §G.a.ix, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty will review the OSDP version 2.2 requirements with Meta to determine compliance with, deviation from, or exception to specific requirements within the document. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
23 | Security | §G.b.i | Access Control: Meta leased space shall be access-controlled using either a multi-factor authentication (2-fac) or single-factor authentication (1-fac) approach. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.ii | Access Control: Multi-factor authentication requires two different types of identify factors to enter: (1) Something you have (e.g., Card, Key, etc.) AND EITHER (2) Something you know (e.g., PIN, Username/Password) or (3) Something you are ( e.g., Fingerprint, Facial Geometry, etc.). | Base Build (part), TFO (part) | Comply |  | Landlord standard multi-factor authentication is card-key plus biometric access control. Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.iii | Access Control: Single-factor identification is used for all access-controlled doors not implementing a multi-factor approach. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.iv | Access Control: The type of access control provided for entry and exit of Meta leased space shall be dictated by the Meta's space type requirements (Refer to Device Matrix). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v | Access Control: 2-factor authentication in and 1-factor authentication out shall be used in spaces that are designated as high-risk and/or critical to the success of the operation (Refer to Device Matrix). These spaces shall be designated by the Meta and include but not limited to: | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v.1 | Access Control: All spaces with access to or are part of the Metas’s network (e.g. MDF, Network Suite, Data Hall, IDF, etc.). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v.2 | Access Control: High-value assets and/or equipment that will transmit or store user data is present (e.g. IBOS storage). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v.3 | Access Control: The doorway is an entry to Meta’s leased space housing core datacenter infrastructure (e.g., Production Network spaces, Data Halls, etc.). | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v.4 | Access Control: General controls for the entire building’s facility operations systems are present. This includes but is not limited to spaces in which FacNet network switches or FacNet Client devices are present. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v.5 | Access Control: All doors into ERAD spaces | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.v.6 | Access Control: Controls for the entire building’s security systems are present | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.vi | Access Control: If none of the above 2-factor conditions exist, a minimum of 1 factor of identity authentication shall be provided where one or more of the following conditions exist (Refer to Device Matrix): | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.vi.1 | Access Control: Controls for a portion of the security systems of the building are present | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
23 | Security | §G.b.vi.2 | Access Control: Physical security keys to the building are present. | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §G.b.vi.3 | Access Control: Mechanical equipment, electrical equipment, or other controls are present which could impact operations in a portion of the building | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §G.b.vi.4 | Access Control: Spaces which store equipment, spares, and other materials which are critical to data center operations | Base Build (part), TFO (part) | Comply |  | Dual-factor authentication access control for Meta leased data halls and Landlord POP rooms will be provided as part of the Base Building scope-of-work. All other facility doors will have single-factor authentication access control provided as part of the Base Building scope-of-work. Access control for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §G.b.vii | Access Control: All access-controlled doors shall be actively monitored with an alerting mechanism that sends an alarm to on-site security personnel when unauthorized access is detected. This includes door forced open, door held open, etc. | Base Build (part), TFO (part) | Comply |  | Monitoring for data hall, POP room, electrical room, mechanical gallery, ancillary space, and other access controlled area doors will be provide as part of the Base Building scope-of-work. Monitoring for Meta leased office, storage, ancillary space, or sub-divided space (including data hall cage) doors will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §G.b.viii | Access Control: All doors shall "fail secure" unless required for life safety egress. Doors that must "fail safe" for life safety egress shall have access control installed on the egress side that only acts to shunt the door alarm. | Base Build (part), TFO (part) | Comply |  | Landlord's standard is to have all doors "fail secure" except where required by local code or AHJ's for life safety egress. Data hall, POP room, electrical room, mechanical gallery, ancillary space, and other facility doors will be provide as part of the Base Building scope-of-work. Doors within Meta leased office, storage, ancillary space, or sub-divided space (including data hall cages) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §G.b.ix | Access Control: The access control system shall adhere to OSDP version 2.2 (or latest). Encryption (Secure Channel) shall be enabled and reader tamper alarm monitoring shall be employed. | TFO | Comply (part); Deviation (part); Exception (part) |  | Compliance with, deviation from, or exception to access control system requirements per OSDP version 2.2 or the latest version will be determined as part of Tenant Fit-Out (TFO) scope-of-work. Installation of access control system equipment to support each particular requirement of OSDP version 2.2 or the latest version will correspond with that particular requirement's "comply" versus "deviation" versus "exception" status. |  | Meta | 2 |  | No response received from Meta. Digital Realty will review the OSDP version 2.2 requirements with Meta to determine compliance with, deviation from, or exception to specific requirements within the document. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
24 | Security | §A.a | Video Surveillance: General | Base Build (part), TFO (part) | Comply |  | See comments to §A.a.i through §A.a.iii, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §A.a.ii | Video Surveillance: All building exterior entrances/doors shall have Landlord provided identification-level video surveillance coverage to monitor egress and ingress. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §A.a.ii | Video Surveillance: All aspects of video surveillance within and outside Meta leased space shall be provided, managed, and maintained by the Landlord. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §A.a.iii | Video Surveillance: Landlord shall provide identification level coverage (Pix/ft density of at least 50) of access-controlled doors from Landlord space into Meta space and vice versa. | Base Build (part), TFO (part) | Comply |  | Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to video surveillence systems and devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
24 | Security | §A.b | Video Surveillance: Meta Leased Space/Fit-Out | TFO | Comply |  | See comments to §A.b.i through §A.a.vi, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
24 | Security | §A.b.i | Video Surveillance: Meta leased space requires a layered video surveillance approach dependent on conditions within the space. This approach uses three classifications of coverage: (1) Overview level - (greater than 10 pix/ft density), (2) Recognition Level – (greater than 20 pix/ft density), (3) Identification Level – (greater than 50 pix/ft density) | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
24 | Security | §A.b.ii | Video Surveillance: The location, number of cameras, and performance level of each camera within Meta leased space shall be dictated by the Meta's space type requirements. (Refer to Device Matrix) | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
24 | Security | §A.b.iii | Video Surveillance: Overview level coverage shall be provided in spaces that hold high value assets or where work on high value assets is being done. (IBOS, Spoke, ERAD, etc.). These spaces shall have full coverage with no blackout or dead areas. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
24 | Security | §A.b.iv | Video Surveillance: Recognition level coverage (greater than 20 pix/ft density) shall be provided in the Data Hall. Cameras shall provide coverage throughout main aisles. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
24 | Security | §A.b.v | Video Surveillance: ERAD spaces require specific coverage which includes: | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
25 | Security | §A.b.v.1 | Video Surveillance: Identification level coverage of all working stations with a minimum 1 frame per section (FPS) when no motion detected, and 10 FPS when motion is detected. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
25 | Security | §A.b.v.2 | Video Surveillance: Cameras shall work with very low light (night vision mode) and shall have a sensitivity set to 5 percent motion detection. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
25 | Security | §A.b.v.3 | Video Surveillance: Cameras in the ERAD room(s) should be set to continuously record. | TFO | Comply |  | Video surveillence within Meta leased space will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
25 | Security | §A.b.vi | Video Surveillance: Any Landlord IDF supporting the video management system for the Meta’s space shall be located outside of the Meta’s leased space. | Base Build | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
25 | Security | §B.a | Intrusion Detection and Resistance: Devices | Base Build | Comply (part); Deviation (part) |  | See comments to §B.a.i through §B.a.iv, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
25 | Security | §B.a.i | Intrusion Detection and Resistance: All Meta dedicated spaces with glazed openings within 10ft. (3 m) of grade shall be laminated glass OR be provided with an anti-shatter film that is reviewed and approved by the Meta. | Base Build | Comply |  | Base Building glazing will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Laminated glass or anti-shatter film will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
25 | Security | §B.a.ii | Intrusion Detection and Resistance: Intrusion detection capability shall be provided at all exterior doors (e.g. door held open and door forced open detection) to establish a secure building perimeter layer. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
25 | Security | §B.a.iii | Intrusion Detection and Resistance: Intrusion detection capability shall be provided at all access controlled doors to detect and alert of unauthorized access. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
25 | Security | §B.a.iv | Intrusion Detection and Resistance: The Landlord shall provide intrusion detection devices to monitor all man passable openings (e.g., louvers, hatches, etc.) into Meta leased space that are not physically secured to prevent unauthorized access (e.g., tamper-resistant fasteners, physical locks, etc.). | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Dalton Rosenberger
25 | Security | §B.b | Intrusion Detection and Resistance: Construction | Base Build (part), TFO (part) | Comply |  | See comments to §B.b.i and §B.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Items for §B.b.ii, below, will be paid for by Meta as part of TFO NRCs. | N/A
25 | Security | §B.b.i | Intrusion Detection and Resistance: Where other tenants share a wall with Meta’s high-risk spaces, such walls shall extend below the raised access floor to the slab and to the ceiling by means of security grade wire mesh or other industry recognized secure barrier. Further such walls must be alarmed to detect intrusion. | Base Build | Comply |  | No applicable as Meta is the only tenant in the Building. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. This item is not applicable since Meta is the only tenant in the Building. | N/A
25 | Security | §B.b.ii | Intrusion Detection and Resistance: ERAD room design shall incorporate visual privacy features to prohibit visibility from outside of Meta Space | TFO | Comply |  | Visual privacy features for ERAD room(s) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
25 | Security | §C.a.i | Network Security: Network Access: Any device not owned and approved for use by Meta shall not be connected to any Meta network. (e.g., laptops, computers, cameras, BMS devices, EPMS devices, etc.) | TFO | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | N/A
25 | Security | §C.b.i | Network Security: Network Interconnections: The Landlord’s, other tenant, or any other network shall not be connected to any Meta network. | TFO | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | N/A
25 | Security | §C.c.i | Network Security: Network Interconnections: Network equipment, patch panels, interconnections, splice enclosures or telecommunication outlets, other than those owned or operated by Meta, shall not be collocated in a space or room containing those owned or operated by Meta. | Base Build (part), TFO (part) | Deviation |  | Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. |  | Meta | 3 |  | No response received from Meta. Digital Realty confirms that Building POE and POP rooms will be used by Meta, Landlord, and 3rd party telecommunications carriers | Jason Brunen
26 | Security | §C.c.ii | Network Security: Network Interconnections: An exception to the above may be granted by the Meta for spaces where the Meta’s fiber infrastructure is intended to connect to carrier equipment. | Base Build (part), TFO (part) | Deviation |  | Building POE and POP rooms may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. |  | Meta | 3 |  | No response received from Meta. Digital Realty confirms that Building POE and POP rooms will be used by Meta, Landlord, and 3rd party telecommunications carriers | Jason Brunen
26 | Security | §C.c.iii | Network Security: Network Interconnections: All video surveillance and access control devices shall be routed back to the Landlord’s IDF. There shall be no devices that connect to a Meta IDF, this includes devices that are located within the Meta’s leased space. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
26 | Security | §C.c.iv | Network Security: Network Interconnections: All cabling that supports video surveillance and access control shall be physically separated from Meta network cabling. This includes devices that are located within the Meta’s leased space. | Base Build (part), TFO (part) | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | N/A
26 | Security | §C.d.i | Network Security: Telecommunication Pathways and Vaults between Meta-Lease Spaces: Exterior telecommunications pathways used to connect multiple Meta-leased spaces shall be secured and protected from unauthorized access. The Landlord shall be able to detect when those spaces are accessed. | Base Build (part), TFO (part) | Comply (part); Deviation (part) |  | As part of the Base Build, Landlord has allowed for standard 8' x 10' telecommunications vaults which do not feature locking covers or instrusion detection. Telecommunications vaults which are larger in size and feature locking covers and instrusion detection alarms can be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty has provided costs to modify the OSP vaults, manhole openings, security monitoring, access control, and duct bank conduit quantities. Any modifications to Landlord's baseline installations will be paid for by Meta as part of TFO NRCs. | Jason Brunen
26 | Security | §C.d.ii | Network Security: Telecommunication Pathways and Vaults between Meta-Lease Spaces: The Landlord shall notify Meta: (1) Before such a space is scheduled to be accessed so that Meta can monitor the network for intrusion, (2) Immediately when unscheduled access to such a space occurs. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. | N/A
26 | Security | §D.a | Device Matrix: High Risk Spaces Includes table listing (11) space types and their associated access control and video surveillance requirements. | Base Build (part), TFO (part) | Comply |  | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
27 | Security | §D.b | Device Matrix: Low/Medium Risk Spaces Includes table listing nine (9) space types and their associated access control and video surveillance requirements. | Base Build (part), TFO (part) | Comply |  | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
27 | Security | §D.Notes | Device Matrix: Notes: • Where there is an interconnecting door between the Network Hub and Megapod, Network Hub shall be 2-fac in, and 1-fac out into the Megapod • There shall be no designated path of egress from the Megapod through the Network Hub unless required by the AHJ and approved by Meta • Where a space requires 2-FAC and shares an interconnecting door with another Meta controlled space, it shall have 1-FAC access control in and out. • When a space requiring 2-fac shares an interconnecting door with another Meta space it shall have 1-factor access control installed on both sides. • Overview level - (greater than 10 pix/ft density), Recognition Level – (greater than 20 pix/ft density), Identification Level (ID) – (greater than 50 pix/ft density) | Base Build (part), TFO (part) | Comply |  | Base Building access control device type, location, and functionality and Base Building video surveillance resolution, device type, and device location will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. Any changes or additions to access control systems & devices and video surveillence systems & devices will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Any modifications to Landlord's baseline security installations will be paid for by Meta as part of TFO NRCs. | Dalton Rosenberger
27 | Connectivity | §E.a | OSP Pathway: Carrier Pathways | Base Build | Comply |  | See comments to §E.a.i through §E.a.iv, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
27 | Connectivity | §E.a.i | OSP Pathway: Pathways are to be provided to allow for outside carriers to enter facility from 4 diverse entry points | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
27 | Connectivity | §E.a.ii | OSP Pathway: Require minimum of 25’ separation between 4 diverse pathways | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.a.iii | OSP Pathway: Meta requires latitude/longitude to be provided for vault entry points to the campus duct ring. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.a.iiv | OSP Pathway: Required to provide outside carriers with location to tie into the campus to provide service | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b | OSP Pathway: Production Pathways | Base Build | Comply |  | See comments to §E.b.i through §E.b.ii, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b.i | OSP Pathway: Pathways are to be provided to interconnect the fiber cabling between buildings 1 through 3 for the back end (BE) and Front End (FE) network. | Base Build | Comply |  | There are only two (2) buildings on the campus. Production pathways will be provided to connect these buildings. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b.i.1 | OSP Pathway: BE Network | Base Build | Comply |  | See comments to §E.b.i.1.a, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b.i.1.a | OSP Pathway: There shall be a requirement of 2 diverse entry points with a required minimum of 25’ separation between the 2 diverse pathways. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b.i.2 | OSP Pathway: FE Network | Base Build | Comply |  | See comments to §E.b.i.2.a, below. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b.i.2.a | OSP Pathway: There shall be a requirement of 4 diverse entry points with a required minimum of 25’ separation between the 4 diverse pathways. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §E.b.ii | OSP Pathway: Meta requires latitude/longitude to be provided for vault entry points to the campus duct ring. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | N/A
28 | Connectivity | §F | ISP Pathways | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.a. through §F.b.iii.4.b.iv, below. |  | -- | 1 |  | Header item only. | N/A
28 | Connectivity | §F.a | ISP Pathways: ISP Pathways Supporting OSP | Base Build (part), TFO (part) | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.a.i through §F.a.ii.5, below. |  | -- | 1 |  | Header item only. | N/A
28 | Connectivity | §F.a.i | ISP Pathways: ISP Pathways Supporting OSP: Supporting Spaces | TFO | Comply |  | Compliance to requirements will be provided as part of Tenant Fit-Out scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
28 | Connectivity | §F.a.i.1 | ISP Pathways: Refer to the Building Interior and Structure section for space allocation and sizing requirements. | TFO | Comply |  | Compliance to 'Building Interior and Structure' section ISP pathway space quantity and sizing requirements will be provided as part of Tenant Fit-Out scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
28 | Connectivity | §F.a.i.2 | ISP Pathways: Meet Me Room ("MMR") | TFO | Comply |  | See comments to §F.a.i.2.a through §F.a.i.2.c, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
28 | Connectivity | §F.a.i.2.a | ISP Pathways: Each MMR requires 4 racks to be reserved for Meta use. These shall be (4) CPI 4-post racks. Refer to Power section for rack electrical requirements. | TFO | Comply |  | CPI 4-post racks for Meta use and associated electric power circuits will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
28 | Connectivity | §F.a.i.2.b | ISP Pathways: Landlord responsible for coordinating with Meta carriers and providing a provisioned MMR room in accordance with Meta carrier install schedules. | TFO | Comply |  | Landlord will provide a provisioned MMR room as part of the Tenant Fit-Out (TFO) scope-of-work. Carrier install schedules will be as detailed with the Lease. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
28 | Connectivity | §F.a.i.2.c | ISP Pathways: Pathways from MMR to Network Suites shall be designed by Meta. Installation of pathways shall be coordinated with Meta during design. | TFO | Comply |  | Pathways from MMR to Network Suites will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
28 | Connectivity | §F.a.ii | ISP Pathways: Entrance Facilities ("EF") | TFO | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.a.ii.1.a through §F.a.ii.5, below. |  | -- | 1 |  | Header item only. | N/A
28 | Connectivity | §F.a.ii.1 | ISP Pathways: All OSP conduits stubbing up into room to be coordinated with Meta. | Base Build | Exception |  | OSP conduit stub-up locations will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. |  | Digital Realty | 3 |  | No response received from Meta. Digital Realty confirms that OSP conduit stub up locations will be determined by Landlord. Item will be paid for by Digital Realty as part of Base Build. | Jason Brunen
28 | Connectivity | §F.a.ii.2 | ISP Pathways: Room walls shall be covered with fire-rated plywood. | Base Build | Comply |  | No comment. |  | Digital Realty | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Digital Realty as part of Base Build. | Dan Kingman
28 | Connectivity | §F.a.ii.3 | ISP Pathways: Rooms are to be dedicated to Meta use. | Base Build | Deviation |  | Building entrance rooms (EF, POE, and POP rooms) may house network equipment, patch panels, interconnections, and splice enclosures owned and operated by Meta, Landlord, 3rd party telecommunications carriers, and 3rd party service providers. |  | Meta | 3 |  | No response received from Meta. Digital Realty confirms that Building entrance rooms (Efs, POEs, POP rooms) will be used by Meta, Landlord, and 3rd party telecommunications carriers | Jason Brunen
28 | Connectivity | §F.a.ii.4 | ISP Pathways: All ladder racks and trays in the room shall be designed and installed by Meta. | TFO | Comply |  | Building entrance rooms (EF, POE, and POP rooms) will have ladder rack and/or fiber tray designed and installed by Landlord as part of the Base Build scope-of-work. Redesign and moves-adds-changes for ladder racks and/or fiber trays can be provided Meta as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Per this requirement, Digital Realty response is changed to "Comply" and we confirm that all ladder racks and trays in Entrance Facilities (EF) shall be designed and installed by Meta | Dan Kingman
28 | Connectivity | §F.a.ii.5 | ISP Pathways: If the DC is a multistorey facility, the EF room shall also be utilized as a riser for OSP and ISP fiber. LL to provide all associated knockouts and pathways. | Base Build (part), TFO (part) | Comply |  | The building is a two (2) storey facility. Utilization of the building entrance rooms (EF, POE, and POP rooms) as a riser and engineering, furnishing, and installing pathways (and associated knockouts, core drilling, and other penetrations) will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 2 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b | ISP Pathways: ISP Pathways | TFO | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.b.i through §F.b.iii.4.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.i | ISP Pathways: Cabling to support Front End (FE), Back End (BE), and General Systems (GS) shall be supported by ladder tray (Tier-1), Cable Trough (Tier-2), and basket tray (Tier-3, Tier-4, Tier-5, and Tier-GS). These tray tiers shall be implemented as needed to support the connectivity to/between meta network spaces (Network Suites, Megapods, GSIDF, etc.) and landlord spaces (POE and MMRs). | TFO | Comply |  | Ladder tray, cable trough, and basket tray to support Front End (FE), Back End (BE), and General Systems (GS) cabling will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.ii | ISP Pathways: Key Spaces | TFO | Comply (part); Deviation (part); Exception (part) |  | See comments to §F.b.ii.1 through §F.b.ii.4.b, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Jason Brunen
29 | Connectivity | §F.b.ii.1 | ISP Pathways: Refer to the Power section for power rating requirements per space. | TFO | Comply |  | Compliance to 'Power' section requirements will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.ii.2 | ISP Pathways: Network Suites | TFO | Exception |  | See comments to §F.b.ii.2.a, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Jason Brunen
29 | Connectivity | §F.b.ii.2.a | ISP Pathways: Provide four (4) Network Suites per Region. Network Suites must be able to be connected to each Megapod in the region while maintaining the 25% failure domain requirement. | TFO | Exception |  | Exception is taken to this item as it refers to Meta "Regions" and does not contain any scope-of-work requirements. The number of Network Suites to be provided will be as stated within the Lease. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Jason Brunen
29 | Connectivity | §F.b.ii.3 | ISP Pathways: Megapods | TFO | Exception |  | See comments to §F.b.ii.3.a and §F.b.ii.3.b, below. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Jason Brunen
29 | Connectivity | §F.b.ii.3.a | ISP Pathways: Each Megapod will contain a Main Distribution Frame (MDF) and dedicated IT rows. The MDF is a network space that provides connectivity between Megapods and Network Suites. | TFO | Exception |  | Exception is taken to this item as does not contain any scope-of-work requirements. The number of Megapods, Main Distribution Frames, and dedicated IT rows to be provided will be as stated within the Lease. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Jason Brunen
29 | Connectivity | §F.b.ii.3.b | ISP Pathways: Provide a maximum of forty-eight (48) Megapods per Region. | TFO | Exception |  | Exception is taken to this item as it refers to Meta "Regions" and does not contain any scope-of-work requirements. The number of Megapods to be provided will be as stated within the Lease. |  | Meta | 2 |  | No response received from Meta. Digital Realty takes exception to this requirement since in does not contain any applicable scope-of-work requirements. | Jason Brunen
29 | Connectivity | §F.b.ii.4 | ISP Pathways: Support spaces | TFO | Comply |  | See comments to §F.b.ii.4.a and §F.b.ii.4.b, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.ii.4.a | ISP Pathways: Refer to the Building Interior and Structure section for space quantity and sizing requirements. | TFO | Comply |  | Compliance to 'Building Interior and Structure' section ISP pathway space quantity and sizing requirements will be provided as part of Tenant Fit-Out scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.ii.4.b | ISP Pathways: Refer to the Power section for power rating requirements per space. | TFO | Comply |  | Compliance to 'Power' section requirements will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii | ISP Pathways: GS Spaces | TFO | Comply |  | See comments to §F.b.iii.1 through §F.b.iii.4.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.1 | ISP Pathways: GSIDF | TFO | Comply |  | See comments to §F.b.iii.1.a through §F.b.iii.1.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.1.a | ISP Pathways: Meta uses the standard of determining GSIDF coverage using a diamond centered at the center of the IDF with a diagonal from the center of the diamond to a corner of the diamond with 235’ in length. Anything within the diamond is considered covered by the GSIDF. GSIDFs coverage must contain all Network Suites, Megapods, and common spaces completely. If coverage exceptions are needed, these will require Meta approval. | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.1.b | ISP Pathways: Number of rack positions - 2 | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.1.b.i | ISP Pathways: Rack 01 passive and Rack 02 active. | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.1.b.i | ISP Pathways: iCPI 4-post for all racks | TFO | Comply |  | All GSIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.2 | ISP Pathways: ADMIDF | TFO | Comply |  | See comments to §F.b.iii.2.a through §F.b.iii.2.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
29 | Connectivity | §F.b.iii.2.a | ISP Pathways: ADMIDF coverage is determined in a similar manner as GSIDFs utilizing the diamond coverage method. ADMIDF coverage must include all admin/office space for the floor the IDF is on. ADMIDF coverage is limited to the floor on which the ADMIDF is on. If coverage exceptions are needed, these will require Meta approval. | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.2.b | ISP Pathways: Number of rack positions – 4 | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.2.b.i | ISP Pathways: 2 active (Rack positions 02, 03) and 2 passive (Rack positions 01, 04). | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.2.b.ii | ISP Pathways: CPI 4-post for all racks | TFO | Comply |  | All ADMIDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.3 | ISP Pathways: GSMDF | TFO | Comply |  | See comments to §F.b.iii.3.a through §F.b.iii.3.b.ii, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.3.a | ISP Pathways: Co-located in each Network Suite, Rows 01 and 02. | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.3.b | ISP Pathways: Number of rows in each space - 2 | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.3.b.i | ISP Pathways: Number of rack positions in each row – 23 (Racks 01-03; 21-23 passive; Racks 04-20 active). | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.3.b.ii | ISP Pathways: CPI 4-post for Active Racks and CPI 2-post for Passive Racks. | TFO | Comply |  | All GSMDF racks, rack accessories, electric power circuits, telecommunications pathways, telecommunications pathway accessories, data cabling, data cabling accessories, and all related engineering, installation, labeling, testing, and provisioning work will be provided as part of Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4 | ISP Pathways: Riser Rooms | TFO | Comply |  | See comments to §F.b.iii.4.a through §F.b.iii.3.b.iv, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4.a | ISP Pathways: For carrier and inter-building front-end connectivity, if multi-story building four risers are required to connect MDF spaces across floors. This is achieved by utilizing 4” conduit sleeves. Meta to coordinate the quantity of knockouts required. | TFO | Comply |  | The building is a two (2) storey facility. Engineering, furnishing, and installing risers, riser pathways, and associated conduit sleeves, knockouts, core drilling, and other penetrations will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4.b | ISP Pathways: For intra-building back-end network connectivity, risers shall be placed between back-end MDF pairs. | TFO | Comply |  | The building is a two (2) storey facility. Engineering, furnishing, and installing risers, riser pathways, and associated conduit sleeves, knockouts, core drilling, and other penetrations will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.i | ISP Pathways: Riser configuration and slot dimension to be coordinated with Meta. | TFO | Comply |  | Riser configuration, penetration sizing & dimensions, and coordination with Meta will be determined and provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.ii | ISP Pathways: Preferred dimension 20”x 6” with 6 FT minimum between slots | TFO | Comply |  | Riser configuration, penetration sizing & dimensions, and distance between penetrations will be determined as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.iii | ISP Pathways: If perforations are located within accessible spaces, these must be secured in compliance with safety requirements. | TFO | Comply |  | Riser penetration locations, penetration accessability, and health & safety considerations will be addressed as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §F.b.iii.4.b.iv | ISP Pathways: Location and sizing of penetration zones for ISP pathways shall be coordinated with Meta for clash detection with other systems. | TFO | Comply |  | Riser configuration, penetration sizing & dimensions, and coordination with Meta will be determined and provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
30 | Connectivity | §G | Cabling | TFO | Exception |  | See comments to §G.a through §G.f.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
30 | Connectivity | §G.a | Cabling: All Cabling shall be designed and installed by Meta to meet the network requirements set by pINE and ENS. Cabling design is broken down by use case below and includes any outside plant (OSP), inside plant (ISP) and patch cabling. | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
30 | Connectivity | §G.b | Cabling: Carrier | TFO | Exception |  | See comments to §G.b.i through §G.b.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
30 | Connectivity | §G.b.i | Cabling: Outside Carrier to bring in new service via fiber optic cable to POE and/or MMR to provide lit and dark service for the Meta network | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
30 | Connectivity | §G.b.ii | Cabling: Services Handed off in the POE will tie to a house Meta Carrier cable which will be designed and routed by Meta on Tier-GS from POE to Network Suites. Cabling from a POE shall remain diverse from other POEs going to the same Network Suite. POE shall provide 4 diverse paths to each Network Suite. | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.b.iii | Cabling: Services Handed off in the MMR will tie to a house Meta Carrier cable which will be designed and routed by Meta on Tier-GS from MMR to Network Suites. Cabling from an MMR shall remain diverse from other MMRs going to the same Network Suite. MMRs shall provide a path to each Network Suite to be diverse from any other (minimum of 2 MMR for region) | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.c | Cabling: General Systems (GS) | TFO | Exception |  | See comments to §G.c.i through §G.c.v, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.c.i | Cabling: 2 Network Suites will serve as the main GSMDFs for the region. GS will be a 2- path system for the region, where path 1 comes from one Network Suite and path 2 comes from the other | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.c.ii | Cabling: GS cabling shall be provided between Network Suites | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.c.iii | Cabling: All GSIDF and ADMINIDF shall be numbered in accordance with coordination with ENS | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.c.iv | Cabling: PTP Cabling shall connect to each Network suite providing 4 distinct paths for cabling | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.c.v | Cabling: MGMT and Console Fiber cabling shall be designed to support the production network (Front-End and Back-End) | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.d | Cabling: CorpNet | TFO | Exception |  | See comments to §G.d.i through §G.d.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.d.i | Cabling: All AP layouts shall be designed by Meta-RSE and installed by DEC managed vendors. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.d.ii | Cabling: Overall floorplans, clearly indicating Meta-Exclusive Occupied space for AP layout and integration into Technology Drawing Sets. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.d.ii.1 | Cabling: The “Overall AP Layout Plan” should show walls, doors, cable tray as full-tone and racks, HAC, shelving and room names as half-tone. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.d.ii.2 | Cabling: Once the Overall Plans are provided to the RSE TDM they will send back AP Layouts to be included by the TEOR into the drawings set. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.d.iii | Cabling: In addition the Overall AP Layout Plan will be AP mounting details for all AP mounting types occurring within the space. | TFO | Exception |  | Exception is taken to this requirement as all AP layouts and APs shall be designed, furnished, and installed by Meta or others. Landlord shall have no responsibility for incorporating or integrating AP layouts or mounting details into Landlord's technology drawings. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.e | Cabling: Front-End (FE) | TFO | Exception |  | See comments to §G.e.i through §G.e.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.e.i | Cabling: All Cabling required to connect layers in Network Suites, between Network Suites, and from Network Suites to Megapods | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.e.ii | Cabling: Designed as 4 diverse paths system between network topology layers | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.e.iii | Cabling: Leverages outside designated goalpost in Megapods | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.f | Cabling: Back-End (BE) | TFO | Exception |  | See comments to §G.f.i through §G.f.iii, below. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.f.i | Cabling: All Cabling required to connect layers between Megapods by either direct cabling between megapods and/or cabling from Megapods to Network Suites | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.f.ii | Cabling: Designed as 2 diverse path system between network topology layers | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
31 | Connectivity | §G.f.iii | Cabling: Leverages inside designated goalpost in Megapods | TFO | Exception |  | Exception is taken to this requirement as all cabling shall be designed, furnished, and installed by Meta or others. |  | Meta | 2 |  | No response received from Meta. Per "Connectivity" requirement §G.a, all Cabling shall be designed and installed by Meta | N/A
32 | N/A | N/A | Interior lighting controls sequence of operations Table at top of page #32 | Base Build | Exception |  | Exception is taken to the "Interior Lighting Controls Sequence Of Operations" table at the top of page #32. Lighting controls and lighting controls sequence of operations (SOO) will be as detailed and shown in the Landlord's drawings, plans, specifications, and basis of design. |  |  | 3 |  |  | Jason Brunen
32 | DAS/PTP | §A | Public Safety (ERRCS) DAS | Base Build | Deviation |  | See comments to §A.a through §A.a.iv, below. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §A.a | Public Safety (ERRCS) DAS: Provide a Public Safety DAS system to comply with building and fire code requirements and to ensure first responder radio coverage is provided. | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §A.a.i | Public Safety (ERRCS) DAS: OEM: ADRF or Zinwave | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §A.a.ii | Public Safety (ERRCS) DAS: Active equipment to be UL2524 compliant | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §A.a.iii | Public Safety (ERRCS) DAS: Coordinate with local AHJ on required local frequencies/channels | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §A.a.iv | Public Safety (ERRCS) DAS: Coordinate rooftop antenna location to ensure donor signal functionality | Base Build | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ), a public safety (ERRCS) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a Public Safety (ERRCS) DAS system if required by the AHJ. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §B | Land Mobile Radio (LMR - Handheld radio) System | TFO | Comply |  | See comments to §B.a through §B.c, below. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §B.a | Land Mobile Radio (LMR - Handheld radio) System: Provide Meta personnel used handheld radio system | TFO | Comply |  | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §B.b | Land Mobile Radio (LMR - Handheld radio) System: LMR system may share infrastructure with PS DAS with AHJ approval | TFO | Comply |  | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
32 | DAS/PTP | §B.c | Land Mobile Radio (LMR - Handheld radio) System: OEM: Motorola | TFO | Comply |  | If required, new LMR handheld radio system can be provided for Meta personnel as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty response changed to "Comply". Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §C | Commercial (Cellular) DAS | Base Build (part), TFO (part) | Deviation |  | See comments to §C.a through §C.c, below. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §C.a | Commercial (Cellular) DAS: Provide a cellular DAS solution to ensure in-building cell coverage is adequate and also meets e911 requirements. | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §C.b | Commercial (Cellular) DAS: Landlord to obtain their own signal source from carriers (AT&T, Verizon, T-mobile) | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §C.b.i | Commercial (Cellular) DAS: Recommend over-the-air as temporary and fiber base station installed as permanent | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §C.b.ii | Commercial (Cellular) DAS: Provide a timing source (GPS) to support carrier base stations | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §C.c | Commercial (Cellular) DAS: OEMs: Commscope, Solid, ADRF, Corning | Base Build (part), TFO (part) | Deviation |  | If required by the local Authorities Having Jurisdiction (AHJ) to meet e911 requirements, a commercial (cellular) DAS meeting the intent of these requirements will be provided as part of the Base Build scope-of-work. If not required by the AHJ, Meta may direct Landlord to provide a commercial (cellular) DAS meeting the intent of these requirements as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Digital Realty (if required by AHJ); Meta (if not required by AHJ) | 2 |  | No response received from Meta. Digital Realty confirms that we will install a commercial (cellular) DAS system if required by the AHJ for e911. Otherwise, item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D | Precision-Timing-Protocol (GPS) | TFO | Comply |  | A Precision-Timing-Protocol (GPS) system will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.a | Precision-Timing-Protocol (GPS): Landlord to provide PTP pathway/infrastructure to accommodate 4 (four) PTP antennas | TFO | Comply |  | A Precision-Timing-Protocol (GPS) system with pathway/infrastructure to support four (4) PTP antennas will be provided as part of the Tenant Fit-Out (TFO) scope-of-work. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.b | Precision-Timing-Protocol (GPS): Each PTP antenna is provided by Meta with a pre-terminated cable length attached. Coordinate length with Meta. The antenna OEN is Huber Suhner GPS over fiber. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.c | Precision-Timing-Protocol (GPS): Generally, the PTP antennas terminate to support each network suite (MDF), and coordinate final rack locations with Meta. | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d | Precision-Timing-Protocol (GPS): Landlord to provide two-inch or greater roof penetration with an independent pathway for each network suite | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.i | Precision-Timing-Protocol (GPS): A two-inch mast pipe to mount each antenna | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.ii | Precision-Timing-Protocol (GPS): Cable Containment from the antenna mast to the roof penetration | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.iii | Precision-Timing-Protocol (GPS): Continuous pathway from roof penetration to spaces dedicated for meta use | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.iv | Precision-Timing-Protocol (GPS): All cable pathways must maintain a bend radius of greater than 6 inches | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.v | Precision-Timing-Protocol (GPS): Antennas must be mounted below the nearest lightning arresting air terminal | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.vi | Precision-Timing-Protocol (GPS): At the minimum, a 180-degree view of the southern sky is required | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.vii | Precision-Timing-Protocol (GPS): No obstructions should be within a ten-degree angle from the horizon | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.d.viii | Precision-Timing-Protocol (GPS): The antenna mast should be 6 feet away from metallic reflectors | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman
33 | DAS/PTP | §D.e | Precision-Timing-Protocol (GPS): Due to the class-4 lasers contained within the PTP system, Laser Warning signs should be incorporated into the design of PTP antenna locations | TFO | Comply |  | No comment. |  | Meta | 1 |  | No response received from Meta. Digital Realty confirms that we comply and that no changes are required. Item will be paid for by Meta as part of TFO NRCs. | Dan Kingman